Distribution list

###### The Director (Commercial), GRIDCO, Bhubaneswar.

###### The Director (Operation), OHPC, Bhubaneswar

###### The CGM (O&M), OPTCL, Bhubaneswar.

###### The CGM (Const.), OPTCL Bhubaneswar.

###### The CGM (RT&C), OPTCL, Bhubaneswar.

###### The CGM (PP), GRIDCO, Bhubaneswar.

###### The CGM (Telecom), OPTCL, Bhubaneswar.

###### The CGM (IT), OPTCL, Bhubaneswar.

###### The Sr. G.M (Const)-I, OPTCL, Bhubaneswar.

###### The Sr. G.M (Const)-II, OPTCL, Sambalpur.

###### The Sr. G.M (CPC), OPTCL, Bhubaneswar.

###### The Sr. G.M (CP), OPTCL, Bhubaneswar.

###### The Sr. G.M. (O&M), Zone-I, Narendrapur.

###### The Sr. G.M.(O&M), Zone-II, Meramundali.

###### The CEO, CESU, Bhubaneswar.

###### The A.O., WESCO Utility, Burla

###### The A.O., NESCO Utility, Balasore

###### The A.O., SOUTHCO Utility, Berhampur.

###### The Member Secretary (GCC), OPTCL.

- The ED, Power Grid Corporation of India, Bhubaneswar.

###### The Sr. G.M. (El.), BHEP, Balimela

###### The A.G.M. (El.), CHEP, Chiplima

###### The Sr. G.M. (El.), UIHEP, Mukhiguda

###### The Sr. G.M. (El.), RHEP, Rengali

###### The D.G.M. (El.), HHEP, Burla

###### The D.G.M. (El.), UKHEP, Bariniput, Koraput

###### The S.E. (O&M), Machhakund

###### The DGM (Elect.),  IbTPS, OPGC, Banharpali.

###### The Vice President (O), IMFA, Choudwar.

###### The D.G.M. (O&M), NTPC (TTPS), Talcher.

###### The AGM (Elect.), JINDAL Stainless Ltd., Duburi

###### The G.M, HINDALCO, Hirakud.

###### The G.M.CPP, NALCO, Angul.

###### The Director, M/s. Jindal Steel & Power Ltd., Angul

###### The AVP-Vedanta Ltd (IPP), Jharsuguda

###### The G.M, Vedanta Ltd (CGP), Jharsuguda.

###### The DGM (Power Distribution), RSP, Rourkela.

###### Joint President, Aditya Aluminium Ltd., Lapanga, Sambalpur

###### The G.M.(Elect.),  Bhusan Steel Limited. Meramundali

###### The G.M. (Elect.), Bhusan Power & Steel Ltd, Budhipadar.

###### The G.M.(Elect.), IFFCO Limited.

- Director & COO, GMR Kamalanga Energy Limited, Satyanagar, Bhubaneswar.

- The CEO, Bhubaneswar Power Pvt. Ltd, IRC Village, Nayapalli, Bhubaneswar

## Odisha Power Transmission Corporation Ltd. Bhubaneswar.

Minutes of 98th PSOC meeting held on 11.06.2016 at Panthanivas, Chandipur

List of participants is at Annexure.

Chief Operating Officer, NESCO Utility welcomed all the delegates for taking the pain of attending the PSOC meeting at Chandipur on sea.

Chief Load Despatcher, SLDC, OPTCL welcomed all the participants to the 98th Power System Operational Coordination meeting and highlighted the system performance during the month of May’2016 and overall power scenario of the State. He also emphasized on the drawal by all the Discoms during the month.

The meeting was chaired by Director (Commercial), Gridco.

D.G.M. (SS), SLDC took the agenda items for discussion.

The review proceeded as follows:

1: Confirmation of minutes of 97th PSOC meeting held on 17.05.2016

The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2015/1489(44) dated 28.05.2016 to all the members and also uploaded in the SLDC website. No comment has been received from any of the members.

Deliberation in the meeting:

Since no comments have been received from the members, the minutes of 97th PSOC meeting was confirmed.

PART A: List of items

List of items to be discussed in the meeting are given in the subsequent parts

PART B : SYSTEM PERFORMANCE

B1: Review of Grid Performance for the month of May’2016.

## (A)  Frequency

It was noticed that, during the month of May’16, 75.53 % of times the frequency remained in the IEGC band i.e.  49.90Hz - 50.05Hz in comparison to 71.66 % during the month of  April’16. The maximum and minimum System frequency during the month was 50.41Hz & 49.56 Hz respectively.

## (B)  Grid demand

Grid demand for the month of  May’16 was reviewed. The average consumption during the month was 3130 MW. The maximum System demand of 3965 MW occurred on 18.05.16 at 20:00 Hrs and minimum demand of 1815 MW occurred on 21.05.16 at 22:00 Hrs.

Deliberation in the meeting

It is observed that the average demand during the month of  May’ 16 was decreased by 103 MW and the peak demand  was decreased by 132 MW from that of April’16. The average energy consumption during the month has been increased by 53 MW in comparison to May’15.

(C)  Voltage Profile of important Sub Stations in OPTCL System during the month of May’16.

The Voltage profile at different 220 kV buses in OPTCL system during the month of May’16 was reviewed.

Deliberation in the meeting:

The maximum Voltage of 243.40 kV occurred at Jaynagar 220 kV bus while Narendrapur, 220 kV bus has experienced the minimum Voltage of 171.12 kV. Bus Voltages at Samangara and Lapanga could not be incorporated due to non availability of energy meter in those S/Ss.

CGM (O&M) stated that the tender for procurement of energy meters is under process. Narendrapur Voltage profile can be improved after charging of Pandiabili PG S/S.

[Action: CGM (O&M)]

(D) Loading of 220/ 132 kV Auto at 220 kV S/Ss in OPTCL system for the month of May’16.

Auto loading of all 220 kV S/Ss was reviewed. It was noticed that some of the ICTs have not been provided with energy meter.

Deliberation in the meeting:

It was deliberated that tender for procurement of Energy Audit meters has already been placed.

[Action: CGM (O&M)]

(E) DISCOM Drawal during the month of May’16

The schedule and actual energy drawal by Discoms for the month of May’16 was reviewed.

Deliberation in the meeting:

It was noticed that WESCO had overdrawn 19.649 MU followed by NESCO Utility 7.886 MU during the month, while Southco Utility has under drawn 9.253 MU during the month. CESU’s energy dawal was as per the schedule energy. SLDC stated that there is a demand dip between 17:00 to 18:00 hrs each day resulting power injection to the Grid. Director (Commercial) advised all Distribution Utilities not to impose regulation during the period; rather they should try to get benefit out of the frequency condition during the period.

Southco stated that they had under drawn due to frequent load loss.

[Action: All Distribution Utilities / SLDC]

(F) Energy Generation / import during the month of May’16

Energy generation and exchange during the month of  May’16 was reviewed. The total quantum of energy drawn from all the generation sources including Central Sector Share and CGP/IPP support during the month was 2328.73 MU.

(G) Drawal of Machhakund Power during the month of May’16

The drawal of Machhakund power during the month of May’16 was 39.574 MU against AP drawal of 54.132 MU.

Deliberations in the meeting:

Director (Commercial) stated that Sr. GM (O&M) -I should explore optimization of Machhakund drawal. OHPC should raise the issue in the monthly joint meeting with Machhakund authority. Sr. G.M(O&M)-I should also participate in the monthly meeting.

Southco may take initiative for installation of breaker for its distribution feeders emanating from Machhakund PH to prevent the units from tripping due to fault at distribution network.

Southco stated that inspection of 33 kV Akhusing –Gumuda feeder has been charged.

SLDC stated that the offer of M/s Chemtrol for installation of RVDU at Jayanagar control room, forwarded by CGM (Telecom), has already been sent to CMD.

[Action: Sr.GM (O&M)-I / OHPC / Southco / Gridco / SLDC]

(H) Under Frequency relay operation in OPTCL System during the month of May’16.

There is no UF Relay operation occurred during the month of May’16 as the frequency had never gone beyond 48.50 Hz.

- Status of Open Access applications during the month of May’2016

Status of Open Access Applications received and disposed by SLDC was reviewed.

PART C – Issues to be raised in 121th OCC meeting of ERPC scheduled on 23.05.16

C.1: Implementation of Automatic Demand Management Scheme

OPTCL vide mail dated 24.02.2016 pointed that Hon’ble CERC vide their order dated 31.12.2015 passed in Sou-motu Petition No.- 5/SM/2014 in the matter of non-compliance of Regulation 5.4.2 (d) of IEGC directed all Respondents (SLDCs) for implementation of ADMS in their respective control area. CERC have allowed dead line till 30.06.2016 to the Respondent for implementation of ADMS. Failing which they will be liable for action under Section 142 of the Act.

In 119th OCC, advised all the SLDCs to implement the ADMS in their respective control area by 30.06.2016.

Subsequently, on request from DVC & WBSEDCL, ERPC vide letter dated 05.04.2016 requested Powergrid to take up the issue for inclusion of DMS/ADMS application software in the new SCADA system under new ULDC project which would be of great help for the ER constituents in implementing the ADMS system in their respective control area and subsequent compliance of CERC directive

In the special PRM meeting held on 07.06.2016 at ERPC, Kolkata, the issue of adding “Load Shed Support (LSS)” feature in the 30nos of newly installed Chemtrols RTU in OPTCL system was raised. Powergrid expressed its inability to incorporate the same, as the project of OPTCL has already been completed.

In response to the offer for providing consultancy, two numbers firms have given presentation on dated 03.06.16 at PTC, Chandaka. The evaluation is under process.

Deliberations in the meeting:

SLDC stated that offer for financial bid has been invited from the participants. CGM (Telecom) stated that, tender for 60 nos. of RTUs have been done, incorporating the LSS features.

[Action: SLDC/ CGM (Telecom)/O&M]

C.2: 220 kV inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG), Keonjhar & Pandiabil S/s

PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha. The status deliberated in the last meeting as detailed.

| Sl. No. | Name of the transmission line | Completion schedule |
| --- | --- | --- |
| 1. | 2 X 315MVA 400/220kV Bolangir S/s |
| a. | LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir S/S. | 7 out of 14 completed. Severe ROW problem. Negotiation under progress. |
| b. | LILO of one circuit of Katapalli-Sadeipalli 220 kV D/C line at Bolangir S/S. | Charged on 04.05.2016 |
| 2. | 400/220 kV Keonjhar S/S. |
| a. | Keonjhar (PG)-Keonjhar (OPTCL) 220 kV D/C line | Work order for 220 kV S/S at Keonjhar and associated lines is under process. |
| b. | Keonjhar (PG)-Turumunga (OPTCL) 220 kV D/C Line. | Work will be taken up under JICA scheme. |
| 3. | 400/220 kV Pandiabil Grid S/s |
| a. | Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line | Work order placed. |
| b. | LILO of one circuit of Atri-Puri (Samangara) 220 kV D/C line at Pandiabil (PG) | Pandiabili S/S is expected to be completed by July’16. LILO of Atri-Samangra 220 kV line at Pandiabili by July’16. |

[Action: CGM (Const) / CGM (O&M)]

C.3: Restoration of PLCC system of important lines

1)   In 119th OCC, JUSNL informed that the following:

In 220 KV Ramchandrapur-Joda line auto-reclosure has been enabled and termination done in PLCC panels at Ramchandrapur end but due to non-availability of PLCC panels at Joda (OPTCL) end the A/R and PLCC scheme could not be implemented.

Further, it was informed that JUSNL is ready to share their standby PLCC panels (BPL make) with WBPDCL (for Santaldih end) and OPTCL (for Joda end) to complete the PLCC schemes of both the above lines.

OCC advised WBPDCL and OPTCL to accept the JUSNL offer and implement the PLCC scheme at the earliest for both the 220 kV lines.

WBPDCL and OPTCL agreed and nominated their coordinators as follows to complete the work:

2)  For 220 kV Ramchandrapur-Joda line:

Sh. L. Nayak, GM, OPTCL, M.- 943890780, e-mail: ele.lanayak@optcl.co.in

(ERPC Secretariat has issued a fax message vide no. 138 dated 21.03.2016 to JUSNL for taking up the issue with the above nominated coordinators for restoring the PLCC scheme of both the lines at the earliest.)

OPTCL vide mail dated 16.03.2016 informed the PLCC communication status of the important links under OPTCL as follows:

1. Jeypore(PG)-Jayanagar (Commn. in OPGW exists)

2. Rourkela(PG)-Tarkera (Commn. in OPGW exists)

3. Rengali(PG)-Rengali S/Y (Proposal for Commn. in OPGW is pending)

4. Indravati(PG)-Indravati(PH) (Proposal for Commn. in OPGW pending)

5. Baripada(PG)-Baripada ( Tendering in Progress for OPGW)

6. Baripada(PG)-Rairangpur (Tendering in Progress for OPGW)

Deliberations in the meeting:

C.G.M (Telecom) stated that the approved estimate for Sl. 3 & 4 has been sent to CPC for initiating tendering process. CGM (Telecom) stated that they have not received any reply from JUSNL. PSOC decided that JUSNL may be reminded again in his regard.

[Action: CGM (Telecom) / CGM (O&M)]

C.4: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN.

The activity of the preparation of Crisis Management Plan for countering the cyber attacks and its implementation including the Mock Drills, audits etc. is being monitored by CEA regularly in line with crisis management plant of Ministry of Power. Power Utilities (including generation, transmission & distribution utilities) of eastern region are to furnish regularly, the updated status to Chief Engineer, Distribution Planning & Development Division, CEA. NTPC communicated their activity of the preparation of Crisis Management Plan for countering the cyber attacks vide letter dated 2nd August, 2013.

In 113th OCC, Member Secretary informed that during interaction with consultants of Grid Study Committee, NLDC agreed that they will plan for conducting workshops on crisis management plan for Cyber Security and few workshops will also be held in Eastern Region.

In the last meeting, CGM (IT) stated that the draft report has been prepared, which has to be finalized by the consultant. After finalizing the report, a workshop shall be organized by IT.

In the 95th PSOC IT representative stated that tendering for consultancy has been done. It may take one month time.

Deliberations in the meeting:

CGM (IT) stated that tender has already been floated and will be opened on 4th July’2016.

[Action: CGM (IT)]

C.5: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.

In 84th OCC meeting all constituents were requested to interact with BIS with intimation to ERPC and get certified as per CEA direction.

In 85th OCC, NTPC informed that NTPC-Farakka has been certified with IS 18001. Other constituents including OHPC requested to interact with BIS with intimation to ERPC and get certified as per CEA direction. The matter is getting reviewed by highest authorities with top priority.

In the 95th PSOC, O&M stated that BIS, Kolkata have responded to send their offer

Deliberations in the meeting:

O&M stated that the data required by BIS, Kolkata will be furnished.

[Action: CGM (O&M)]

C.6: Dynamic data of Generator Models required in PSSE for Simulations – ERLDC

To carryout proper simulation studies in PSSE, actual generator parameters are required as incomplete or incorrect modeling of generator may not give valid simulation result. Hence all the generating companies are requested to furnish data for generator, exciter, governor, PSS of their all generating units in the format.

In 114th OCC, the house was informed that the formats are available at ERPC website.(www.erpc.gov.in)

OCC advised all the generating utilities to submit the relevant information as per the format.

In the 95th PSOC meeting, OHPC stated that only 30 % data are available with them. SLDC stated that they may forward the data to ERPC / ERLDC. All other generators including CPPs may furnish their data to ERPC.

Deliberations in the meeting:

OPGC and OHPC stated that they will forward the required data with a copy marked to SLDC.

[Action: OHPC/ All generators /CPPs]

C.7: Status of Emergency Restoration System (ERS Towers) for Eastern Region constituents

The latest status of Emergency Restoration System (ERS towers) as well as the future plan of procurement as informed by OPTCL:

 220 kV ERS towers: 42 nos located at Mancheswar, Chatrapur & Budhipadar

 400 kV ERS towers: 2 nos located at Mancheswar.

12 nos. of new 400 kV ERS towers have been approved by Board of Director for procurement in the current financial year.

 Another 16 nos of 400 kV towers accompanied with 6 sets of T&P are required.

In the OCC meeting, ERPC requested to furnish the expected date of delivery for 12 nos. of 400 kV ERS towers

Deliberations in the meeting:

CGM (O&M) stated that Order has been placed for 12 Nos of 400 kV ERS towers. The expected date of delivery will be around one year.

[Action: CGM (O&M)]

C.8: Mock Black start exercises in Eastern Region – ERLDC

It is deliberated that the mock black start exercise in respect of Upper Kolab PH could not be conducted due to tower collapse of 220kV Upper Kolab-Theruvali ckt. As per the schedule, mock black start exercise in respect of Rengali, Upper Indravati & Burla are to be carried out during June-16.

Deliberations in the meeting

OHPC stated that mock black start exercise for Upper Kolab may be conducted in the month of July

[Action: OHPC / SLDC]

C.9: Status of projects funded under PSDF schemes

In the PSDF review meeting held on 29.04.16 at N. Delhi, it was advised to RPCs to monitor the status of all the projects funded by PSDF. Therefore, constituents are requested to update the status of projects which are being funded by PSDF in the prescribed format.

OCC advised to furnish the status to ERPC on monthly basis by end of the first week of each month.

Deliberations in the meeting

It was decided that O&M shall forward the progress report on each month. SLDC shall mail the format to Sr. G.M (O&M)-II.

[Action: CGM (O&M) ]

C.10: Energy Generation data management from Renewable Energy Sources

RES development Division, CEA has been receiving monthly generation details and installed capacity of Renewable Energy Sources from respective SLDCs and other authorized agencies. Some discrepancies have been found in the data as received by CEA and MNRE. Constituents are requested to reconcile/confirmed the correct information at the earliest.

In 120th OCC, all the constituents were advised to submit the data to CEA as per the prescribed format with a copy to ERPC Secretariat.

Deliberations in the meeting

CGM (PP), Gridco stated that they are forwarding the data to CEA each month. However Gridco will mark a copy to ERPC Secretariat.

[Action: CGM (PP), Gridco]

C.11: Compilation of data for meeting Renewable Energy targets of 175 GW by 2020 -- Reference from MNRE

CEA vide letter dated 29.03.16 has referred Ministry of Power letter no. 23/2/2005-R &R(Vol-XI), dated 22.03.2016 & MNRE letter dated 02.03.2016 regarding compilation of data for meeting Renewable Energy targets of 175 GW by 2020.

In 120th OCC, Concerned State Utilities /Generating companies are requested to submit data of their respective control areas by 1st week of May, 2016.

Deliberations in the meeting

It was decided that Gridco shall furnish the data to MNRE / ERPC.

[Action: CGM (PP), Gridco]

PART-D – Operational Issues

D.1: Non-compliance of drawal schedule by DISCOMs

Non compliance of drawal schedule messages issued to Discoms during the month of April’16 was reviewed.

It is noticed that WESCO had overdrawn to the tune of 19.649 MU followed by NESCO to the tune of 7.886MU, while SOUTHCO has under drawn 9.253 MU & CESU has complied the schedule.

Deliberations in the meeting:

Southco stated that their under drawa during the month was due to frequent load loss. All the Discoms were advised to remain in the schedule to maintain grid discipline and security.

[Action: All Discom utilities]

D.2: Revival of Station Transformer for Station Auxiliary supply at Balimela HEP.

It was suggested in earlier meetings for revival of station supply for Balimela HEP from Balimela Grid S/S.

In the 97th PSOC meeting, it was decided that Southco Utility may take action for installation of energy meters for 33 kV Balimela HEP feeder.

Deliberations in the meeting:

Southco  stated that the meter will be installed by end of June’2016.

[Action: Southco Utility]

D.3: Frequent tripping of 220kV Meramundali-Bhanjanagar ckt. on transient fault.

It was noticed that 220kV Meramundali-Bhanjanagar ckt is tripping frequently on transient fault. It is apprehended that the fault may be due to improper earthing of towers, which needs to be checked to avoid such tripping.

Deliberations in the meeting

CGM (O&M) stated that one CT of ckt-I is defective and will be replaced soon. However, necessary action will be taken for ensuring proper earthing of towers to avoid frequent tripping of the line.

[Action: CGM (O&M)]

D.4: Prolonged outage of transmission elements and tentative revival dates

The tentative revival dates of transmission elements are updated in the last meeting are as follows:

| Sl.No | Name of transmission element | Reason of outage | Probable date of revival |
| --- | --- | --- | --- |
| 1 | 132 kV Jayanagar-Sunabeda line | For conversion to double ckt | Charged on 6th June’16. |
| 2 | 220 kV TTPS-Joda ckt-I | Replacement of conductor | June’2016 |
| 3 | 220 kV U.Kolab-Theruvali ckt. | Tower Collapse at Loc-483 | June’2016 |
| 4 | 400kV Meramundali-Mendhasal ckt. | Tower Collapse at Loc-180, 181 & 182 | July’2016 |
| 5 | 400kV Meramundali-New Duburi ckt. | Tower Collapse at Loc-8/0, 8/1 & 8/2 | June’2016 |
| 6 | 400kV Meramundali-Vedanta ckt. | Tower Collapse at Loc-34 | 22th June’16 |

D.5. Maintenance of 400 kV Indravati (OHPC)- Indravati (PG) S/C line.

Indravati(OHPC)-Indravati(PG) 400 kV S/C line was being maintained by Powergrid since commissioning of the line. At present, Powergrid is insisting OHPC / OPTCL for maintenance of the said line. As per Powergrid’s statement, the line and bay at PGCIL end belongs to the then OSEB. A meeting was convened between Powergrid, OPTCL, Gridco and SLDC to resolve the ownership dispute. Powergrid vide their letter dated 19.03.2016, addressed to CGM (O&M) also indicated the same and requested OPTCL to take up the maintenance work. The line was tripped at PG end due to blasting of R-phase CB. OHPC and OPTCL may verify the records and resolve the issue.

In the 97th PSOC meeting CGM (O&M) stated that the meeting with Powergrid could not be held. OPTCL shall convey the meeting again to discuss the issue.

The issue was discussed in the OCC meeting of ERPC. It was decided to hold a meeting between Powergrid, OHPC & OPTCL on 17th June 2016 at Bhubaneswar to resolve all the issues.

Deliberations in the meeting

The issue will be decided in the meeting scheduled to be held on 17.06.2016

[Action: CGM (O&M) / GRIDCO / SLDC/ OHPC]

D.6: Communication issues

Installation of communication equipment by CGPs / Industries.

The status of data communication from CGPs as deliberated in the last meeting is as follows

| Sl. | Name of CGP | Present status |
| --- | --- | --- |
| 1 | M/s IFFCO, Paradeep | Outdoor commissioning work completed. RTU was locally tested. After replacement of the faulty CVT, data will be integrated. |
| 2 | M/s MSP Mettalicks | PLCC / RTU installed. Database has already been prepared by OPTCL. Final RTU integration with OPTCL system by the vendor is awaited. |
| 3 | M/s NINL, Duburi | M/s NINL has requested for Scheme, BOQ for PLCC / SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. |
| 4 | M/s Rohit Ferro tech | PLCC established and inspection by Telecom Engineers completed. Database has already been prepared by OPTCL. |
| 5 | M/s Vedanta Ltd. (IPP), Jharsuguda | Generators data remains suspect most of the times. |

It was decided that GCC, OPTCL may file a case before the OERC through RT&C wing of OPTCL against those CGPs not complying the data communication provisions with SLDC.

Deliberations in the meeting

GCC stated that GCC is preparing for filing case before the OERC.

[Action: GCC / O&M / RT&C/ C.G.M. (Telecom.)]

D.7: Web based drawal / generation scheduling.

LDC is going to implement web based drawal / generation scheduling for Dist. Utilities and State generating stations including IPPs and CGPs soon.

SLDC had organized training on web based scheduling on 11.05.2016 for all the CGPs connected with OPTCL network. The feedback of the CGPs will be forwarded to IT wing.

Deliberations in the meeting:

SLDC stated that the mock scheduling is in place. Feedback shall be issued to IT wing by end of June’2016

[Action: CGM (IT) / SLDC]

D.8: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

The work for Automatic Meter Reading (AMR) for all the interface points is in progress.

It was deliberated that that from 1st March onwards the AMR shall be made “Go live”. Data will be available after one hour lapses of time.

CGM (IT) stated that AMR data for six types of meters has been mailed to GM (SLDC) for checking and acceptance. Action will be taken after acceptance of the data.

It was decided in the 96th PSOC that SLDC will finalize the checking and sent the report to IT by end of April’2016.

In the 97th PSOC meeting SLDC stated that presently the billing is being done without considering harmonics. IT shall convene a separate meeting with TCS, SLDC & GRIDCO to address the issue.

Deliberations in the meeting

IT stated that TCS will complete the data communication by end of June’2016. However the data cannot be used for commercial purpose, rather they are for monitoring purpose only.

[Action: CGM (IT)]

D.9: Software for Deviation charge billing.

Hon’ble OERC may notify “Intra State Deviation settlement and related matters” Regulation at any time. For implementation of the regulation, required software for Deviation Charge billing need to be developed and tested. CGM (IT) may take necessary steps for development of the software.

In the 97th PSOC meeting CGM (IT) stated that CMD has already approved the proposal. IT has invited offer from M/s TCS. SLDC suggested to expedite the software development.

Deliberations in the meeting

IT stated that there are some commercial issues, which need to be discussed separately. Director (Commercial) stated that the issues may be sorted out soon.

[Action: CGM (IT)]

D.10: Agenda by BPPL.

(i)  Due to outage of 132kV Bidanasi-Chandaka and Aarati-Choudwar ckt. evacuation of BPPL generation is being hampered very often causing financial loss.

(ii) CESU has not considered the open access transaction while preparing the bill for TS Alloys, Athagarh.

Deliberations in the meeting

Since the issue is a bilateral, BPPL may take up the matter with CESU.

[Action: BPPL / CESU]

D.11: Agenda by JSL.

(i)  Grid disturbances in 400 KV systems on 23rd May and 31st May. Reliability of power system in Duburi command area is essential for power supply continuity to our critical steel making processes and also generators. Necessary preventive measures to be taken to avoid grid supply interruptions.

(ii) Online G.P.S time synchronization of Interface Meters & Consumer meter will help JSL as an open access entity to match the approved schedules without deviation. It may be appraised about any immediate plan for online GPS time synchronization of APEX meters being taken up by OPTCL.

(iii) Online display of Interface/Consumer meter data at JSL end will help in identifying any mismatch of sending and receiving end data at the earliest and necessary corrective measures can be taken immediately. Necessary infrastructure required may be explored and allowed for installation.

Deliberations in the meeting

CGM (O&M) stated that the interruption at New Duburi was due to tower collapse. OPTCL is taking action for GPS time synchronization of Apex meters. On line meter data for interface / consumer meter is yet to be completed.

[Action: JSL / OPTCL]

D.12: DISCOM Issues

CESU

- CESU has identified technical issues relating to augmentation of EHT S/S capacity, conversion of S/C line to D/C, bay extension at different S/Ss etc.

B.

- Mismatch of SCADA drawal with the billing meter during May’16.

- Fixed data indicated on dashboard may be converted to variable for accurate drawal display.

- Interruption in RVDU data.

- Provision of on line recording of drawal data for CESU on real time basis.

- Gridco to facilitate for realizing the long outstanding dues of CESU from WESCO & NESCO.

- Provision of RVDU at CESU Head quarter.

- Implementation of UI bill instead of deviation charge bill.

Deliberations in the meeting

The issues raised by CESU, has already been discussed in earlier meetings. CESU may come up with new agenda instead of repeating the same issue.

[Action: CESU]

WESCO

- Revision of BST bill by deducting power import by solar projects.

In the 97th meeting Director (commercial) stated that WESCO may contact Gridco to resolve the issue.

- Provision of power drawal by bulk consumers & Open Access transactions in the RVDU.

- Mismatch between one minute and 15 minute drawal data.

Deliberations in the meeting

Director (Commercial) stated that WESCO and Gridco may resolve the issue of revision of BST bill considering the import by Solar projects. WESCO may contact SLDC regarding data mismatch.

[Action: WESCO / GRIDCO / SLDC]

PART E: OPERATIONAL PLANNING

E.1:  Commissioning status of New Transmission elements.

The status of commissioning of new transmission elements is as follows:

| Sl. No | Transmission element details | Present Status |
| --- | --- | --- |
| 1 | Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line | Work has already been started. Expected to be completed by December’ 2016. |
| 2 | Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt | Line is ready and shall be charged after commissioning of 3rd ICT at Mendhasal, which is under progress. ICT is at BHEL factory |
| 3 | Commissioning of 220 kV Bidanasi-Cuttack line | Work in progress and expected to be completed by June’ 2016. |
| 4 | Commissioning of 220/132 kV Cuttack S/S | Work in progress and expected to be completed by June’ 2016. |
| 5 | Commissioning of 132 kV Baripada (PG)-Jaleswar line | Work has already been started, which will be completed by June 2016. |
| 6 | Commissioning of 220/132 kV Kesinga S/S | Work under progress. Expected by December’ 2016. |

Status of Discom’s action plan for power drawal from the S/Ss commissioned / expected to be commissioned in near future.

| Sl. No | Name of the sub-station | Probable month of commissioning | Name of DISCOM | Action taken by Discoms |
| --- | --- | --- | --- | --- |
| 1 | 132/33kV, 2x20 MVA Khajuriakota | July’16 | CESU | Action being taken |
| 2 | 220/33kV, 2x20 MVA Banei | Dec’17 | WESCO Utility | Stayed by Court. |
| 3 | 132/33kV, 2x20 MVA Udala | Dec-17 | NESCO Utility | Line existing |
| 4 | 132/33 kV, 1x12.5 MVA, Mania | Charged | CESU | 33 kV line not done by CESU |

WESCO shall take action for diversion of 11 kV lines from Jharusuguda S/S.

Action: CGM (O&M)/ CGM (Const.) / All Discoms]

E.2: Energy Metering at Hydro stations.

Energy meters have already been installed at all hydro stations. Billing for the OHPC stations, considering the Apex meters is not being done due to some problems in the meters at Rengali PH.except Upper Kolab, is being done from the newly installed energy meters.

Deliberations in the meeting:

OHPC stated that energy meters at Rengali PH for TTPS feeder is not functioning properly and need to be replaced. It was decided that O&M shall take necessary action for rectification of energy meter at Rengali PH.

[Action: O&M / OHPC]

E.3: Installation of Feeder meters at TTPS.

As per the decision taken in earlier meetings and after getting approval from CEA, OPTCL has taken up for installation of meters in all feeders connecting TTPS with the STS.

In the 97th PSOC meeting, TTPS stated that installation of feeder meters shall be completed by end of May’2016.

Deliberations in the meeting

TTPS stated that representative of Secure meter had attended yesterday. It was decided that O&M shall complete the metering process by end of June’2016.

[Action: CGM (O&M)/ GRIDCO/ TTPS]

E.4: Major Events in the month of May’16

04.05.2016: 220 kV Katapali-Bolangir ckt made LILO with Bolangir PG.

05.05.2016:165 MW Power plant of Bhushan Steel Ltd. synchronized with OPTCL network

11.05.2016: 2nd 132/33 kV, 20 MVA Tfr commissioned at Boudh S/S.

E.5: Important Grid Incidences during the month of April’16.

Important Grid incidents during the month of May’16 were reviewed. The incidents need to be analyzed and deliberated in the PCC meeting of ERPC.

[Action: O&M / SLDC]

E.6: Outage of major transmission Elements during the month of May’16. (above 10 hrs).

Outage of major transmission elements above 10 hours during the month of May’16 was reviewed. Most of the outages are for jumper snapping & insulator damage.

Deliberations in the meeting

O&M may take necessary preventive maintenance to avoid jumper snapping & insulator damage

[Action: O&M]

E.7:  Review of Outage Program of State Generators / Transmission elements for the month of July’16:

Tentative Outage programme for State Generators for the month of July’2016 are as follows:

| Sl. | Station | Unit | Period | Remarks |
| --- | --- | --- | --- | --- |
| 1 | Burla | # 6 | 17.02.14 to continue | Programming for R, M & U |
| 2 | Chiplima | # 3 | 15.02.14 to continue | TGB problem and started R,M & U |
| 3 | Balimela | # 1 | 31.01.13 to continue | TGB problem Programming for R,M & U |
| 4 | Upper Indravati | # 3 | 23.11.15 to 30.06.16 | Capital Maintenance |

[Action: OHPC / SLDC]

E.8: Generation Program for the month of July’16.

Generation schedule for the month of July’16 furnished by OHPC are given below.

| Name of Hydro Gen. Station | Generation Programme (MW) | Reservoir Level as on 01.06.15 | Reservoir Level as on 01.06.16 | MDDL | High Flood Reservoir Level |
| --- | --- | --- | --- | --- | --- |
|  | July’16 (1st fortnight) | July’16 (2nd fortnight) |  |  |  |  |
| HPS-I, Burla | 20 | 20 | 604.23ft | 602.50 ft | 590 ft. | 630 ft. |
| HPS-II, Chipilima | 10 | 10 | - | - | - | - |
| Balimela | 185 | 185 | 1484.70 ft | 1476.60 ft | 1440 ft. | 1516 ft. |
| Rengali | 10 | 10 | 117.21 mt 1.78mt mtr mt | 111.22 mt mt | 109.72mtr | 123.5 mtr. |
| U.Kolab | 100 | 100 | 851.23 mt mt | 848.14 mt | 844 mtr | 858 mtr. |
| U. Indravati | 200 | 200 | 632.10 mt | 630.66 mt mt | 625mtr | 642 mtr |
| MKD (O/D) | 30 | 30 | 2718.95 ft | 2716.20 ft | 2685 ft. | 2750 ft. |
| TOTAL | 555 | 555 |  |  |  |  |

[Action: OHPC / SLDC]

E.9: Anticipated power generation and demand for the month of July’2016.

| Sl. No | Discom | Average | Peak |
| --- | --- | --- | --- |
| 1 | CESU | 1000 | 1250 |
| 2 | WESCO | 900 | 1100 |
| 3 | NESCO | 800 | 1000 |
| 4 | SOUTHCO | 400 | 550 |
| 6 | Total | 3100 | 3900 |
| Availability |  |  |
| 1 | Hydro | 550 | 1200 |
| 2 | State Thermal | 750 | 750 |
| 3 | IPP, small hydro &RE | 800 | 800 |
| 4 | ISGS share (including OA) | 1000 | 1100 |
| 5 | CGP support (OA) | 150 | 150 |
| 6 | Total availability | 3250 | 4000 |
| 7 | Surplus / Deficit | 150 | 100 |

All Discom utilities agreed to their demand forecast for the month of July’2016.

PART F: OTHER ISSUES

All members expressed their gratitude to Er. P. K. Pradhan, Director (Commercial), Gridco, who is going to retire from service on superannuation by end of this month for his guidance and advice. PSOC will remember his valuable advices and the foot prints he has left for all times with deep regard.

F.1: The meeting was ended with vote of thanks specially to A.O, NESCO Utility for organizing the meeting at such a beautiful place and the hospitality extended by his team.

F.2:  Date and Venue of the next (99th) PSOC meeting

It was decided that the 99th PSOC meeting will be held under the aegis of WESCO Utility. WESCO Utility was requested to confirm the same through a letter to CLD, SLDC.

Annexure

List of participants in the 98th PSOC meeting dated 11.06.2016