Odisha Power Transmission Corporation Ltd.

Bhubaneswar.

# Agenda

for

84th Power System Operational Coordination Meeting

## Date: 26.03.2015

### Venue: PTC, Chandaka

Odisha Power Transmission Corporation Ltd. Bhubaneswar.

Agenda for 84th PSOC Meeting to be held on 26.03.2015 at PTC, Chandaka

A1: Confirmation of the minutes of the 83rd PSOC Meeting held on 24.02.2015

The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2014/638(30), dated 10.03.2015 to all the members and also uploaded in the SLDC website. No comment has been received from any of the members.

Members may offer their comments. If there is no comment, the minutes of the meeting may please be confirmed.

PART B: GRID PERFORMANCE

B1: Review of Grid Performance for the month of January’15.’ & February’15.

- Frequency:

Hourly frequency variation for the month of January’15 & February’15.

| Month | % of time frequency remained |
| --- | --- |
|  | <49.00 | 49.00-49.70 | 49.70-49.90 | 49.90-50.05 | >50.05 | 49.70-50.05 |
| Jan’15 | 0.00 | 0.43 | 15.03 | 51.40 | 33.14 | 66.43 |
| Feb’15 | 0.00 | 0.13 | 10.34 | 57.36 | 32.17 | 67.70 |

Maximum & Minimum frequency during the month of January’15 & February’15.

| Month | Freq (Hz) | Date | Time |
| --- | --- | --- | --- |
| Jan’15 | Maximum – 50.56 | 01.01.15 | 03:04 Hrs |
|  | Minimum – 49.56 | 15.01.15 | 07:37 Hrs |
| Feb’15 | Maximum – 50.35 | 17.02.15 | 05:15 Hrs |
|  | Minimum – 49.68 | 17.02.15 | 20:45 Hrs |

- Grid Demand for the month of January’15 & February’15.

| Month | Demand | Maximum Consumption | Maximum Demand | Minimum Demand |
| --- | --- | --- | --- | --- |
|  | MU | MU | Date | MW | Date | Time | MW | Date | Time |
| Jan’15 | 1919 | 64.20 | 23.01.15 | 3464 | 23.01.15 | 20:00 | 1787 | 02.01.15 | 03:00 |
| Feb’15 | 1806 | 68.75 | 26.02.15 | 3613 | 26.02.15 | 20:00 | 1979 | 12.02.15 | 16:00 |
| Feb’14* | 1796 | 66.54 | 25.02.14 | 3468 | 28.02.14 | 20:00 | 1950 | 16.02.14 | 15:00 |

Members may please discuss.

- Voltage Profile of 220 kV Buses in OPTCL system for the month of February’15

| Sl. No | S/s Name | Maximum | Minimum |
| --- | --- | --- | --- |
|  |  | kV | Day | Time | kV | Day | Time |
| 1 | Jayanagar | 247.56 | 7 | 01:45 | 231.40 | 10 | 23:30 |
| 2 | Theruvali | 234.92 | 2 | 13:00 | 210.90 | 10 | 11:30 |
| 3 | Bhanjanagar | 240.75 | 7 | 02:45 | 224.29 | 28 | 18:15 |
| 4 | Chandaka | 236.01 | 12 | 15:30 | 215.98 | 27 | 19:15 |
| 5 | Narendrapur | 234.74 | 8 | 00:15 | 202.76 | 28 | 18:15 |
| 6 | Joda | 241.76 | 16 | 13:30 | 227.63 | 27 | 19:30 |
| 7 | Tarkera | 233.42 | 03 | 04:30 | 224.52 | 12 | 10:00 |
| 8 | Bhadrak | 233.18 | 12 | 03:30 | 209.05 | 25 | 19:15 |
| 9 | Paradeep | 239.30 | 09 | 03:30 | 201.14 | 14 | 04:15 |
| 10 | Budhipadar | 232.49 | 21 | 03:00 | 223.77 | 14 | 16:30 |
| 11 | Duburi | 238.38 | 12 | 15:15 | 218.52 | 28 | 19:00 |
| 12 | Balasore | 239.19 | 13 | 14:15 | 217.14 | 28 | 19:00 |
| 13 | Meramundali | 234.63 | 12 | 13:45 | 225.16 | 28 | 19:00 |
| 14 | Bidanasi | 240.11 | 12 | 14:00 | 218.46 | 28 | 18:30 |
| 15 | Katapalli | 230.18 | 12 | 11:45 | 219.96 | 07 | 10:45 |
| 16 | Nayagarh | 237.69 | 12 | 15:15 | 207.84 | 05 | 11:15 |
| 17 | Mendhasal | 237.63 | 12 | 15:15 | 218.98 | 27 | 19:00 |
| 18 | Bolangir | 239.00 | 18 | 14:00 | 221 | 18 | 10:00 |

The maximum voltage of 247.56 kV occurred at Jayanagar Grid Sub-station while Paredeep 220 kV bus has experienced the minimum Voltage of 201.14 kV.

In the last meeting it was deliberated that at CVT at Meramundali shall be checked and replacement of CVT at Bidanasi will be done. However, Bidanasi  CVT has already been replaced on 28.02.2015.

CGM (O&M) may update and Members may discuss.

- Energy Generation / Import during the month of February’15

| Source of Power | Energy (MU) |
| --- | --- |
| Thermal (TTPS+IB) | 424.54 |
| OHPC Stations including Machhkund share | 343.10 |
| IPP & CGP Support | 399.38 |
| ISGS drawal | 639.36 |
| TOTAL | 1806.38 |

- Drawal of Machhakund Power

The drawal of Machhakund power during the month of February’15 was 29.411 MU against AP drawal of 29.372 MU. Total generation was 61.595 MU.

In the last meeting Sr. G.M (O&M), Zone-I stated that bus modification work at Jayanagar S/S is will be taken up after commissioning of Auto at Jayanagar. G.M (Telecom) stated that installation of OPGW equipments at Machhakund and Jayanagar by POWERGRID is expected to be completed by June 2015. After which, Remote Subscriber (RS) phone provision can be made from Jayanagar S/S. Southco stated that around 1.5 MW load has been extended to Akusingh Grid by linking 33/11kV Substation Kumbhar Dhamuni.  Other linking lines as suitable are being taken up.

In the month of March SLDC & GRIDCO officers had been to Machhakund PH to study the present metering arrangement in view of selling of Machhakund share to AP proposed by GRIDCO. It is proposed to divert the metering cubicle from TTPS to Machhakund PH for proper metering.

Sr. G.M (O&M), Zone-I / GM (Telecom) / Southco / TTPS may update.

- Under Frequency Relay operation in OPTCL System during the month of February’15.

Since the frequency had never gone beyond the lowest setting of UFR, there was no UF Relay operation occurred during the month of February’15.

Members may note

- DISCOM Drawal up to the month of February’15

| Name of DISCOM | Month | Approved Energy Drawal Prorated for the month (MU) | Scheduled Energy (MU) | Actual Energy Drawal ( MU) | Open Access Import Schedule (MU) | Net Energy Drawal ( MU) | Overdraw (MU) |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 1 | 2 | 3 | 4 | 5=(3-4) | 6=(5-2) |
| CESU | Apr’14 | 743.014 | 761.656 | 765.241 | 2.347 | 762.894 | 1.238 |
|  | May’14 | 767.781 | 762.55 | 789.927 | 2.34 | 787.587 | 25.037 |
|  | June’14 | 743.014 | 723.533 | 757.041 | 2.368 | 754.673 | 31.14 |
|  | July’14 | 767.781 | 697.006 | 714.674 | 2.984 | 711.69 | 14.684 |
|  | Aug’14 | 767.781 | 719.368 | 717.87 | 2.984 | 714.886 | -4.482 |
|  | Sept’14 | 743.014 | 693.26 | 725.186 | 1.1704 | 724.0156 | 30.7556 |
|  | Oct’14 | 767.781 | 702.494 | 707.59 | 3.247 | 704.343 | 1.849 |
|  | Nov’14 | 743.014 | 660.172 | 645.803 | 3.586 | 642.217 | -17.955 |
|  | Dec’14 | 767.781 | 623.206 | 620.432 | 4.589 | 615.843 | -7.363 |
|  | Jan’15 | 767.781 | 550.534 | 609.616 | 3.387 | 606.229 | 55.695 |
|  | Feb’15 | 693.479 | 522.025 | 573.657 | 4.571 | 569.657 | 47.632 |
| WESCO | Apr’14 | 560.548 | 597.757 | 631.236 | 17.912 | 613.324 | 15.567 |
|  | May’14 | 579.233 | 636.485 | 649.787 | 21.92 | 627.867 | -8.618 |
|  | June’14 | 560.548 | 582.247 | 630.606 | 9.702 | 620.904 | 38.657 |
|  | July’14 | 579.233 | 546.269 | 611.128 | 27.784 | 583.344 | 37.075 |
|  | Aug’14 | 579.233 | 582.062 | 611.545 | 21.698 | 589.847 | 7.785 |
|  | Sept’14 | 560.548 | 612.084 | 643.179 | 20.574 | 622.605 | 10.521 |
|  | Oct’14 | 579.233 | 616.196 | 651.926 | 26.424 | 625.502 | 9.306 |
|  | Nov’14 | 560.548 | 590.951 | 583.831 | 2.621 | 581.21 | -9.741 |
|  | Dec’14 | 579.233 | 539.112 | 573.154 | 4.289 | 568.865 | 29.753 |
|  | Jan’15 | 579.233 | 514.264 | 552.055 | 4.822 | 547.233 | 32.969 |
|  | Feb’15 | 523.178 | 488.818 | 518.347 | 14.665 | 514.347 | 25.529 |
| NESCO | Apr’14 | 438.082 | 425.340 | 464.947 | 23.735 | 441.212 | 15.872 |
|  | May’14 | 452.685 | 414.293 | 475.678 | 19.668 | 456.01 | 41.717 |
|  | June’14 | 438.082 | 391.799 | 458.494 | 33.207 | 425.287 | 33.488 |
|  | July’14 | 452.685 | 398.217 | 476.175 | 31.676 | 444.499 | 46.282 |
|  | Aug’14 | 452.685 | 447.333 | 451.265 | 22.476 | 428.789 | -18.544 |
|  | Sept’14 | 438.082 | 423.846 | 444.946 | 18.474 | 426.472 | 2.626 |
|  | Oct’14 | 452.685 | 418.854 | 445.698 | 20.311 | 425.387 | 6.533 |
|  | Nov’14 | 438.082 | 366.485 | 393.515 | 23.372 | 370.143 | 3.658 |
|  | Dec’14 | 452.685 | 396.403 | 404.228 | 21.769 | 382.459 | -13.944 |
|  | Jan’15 | 452.685 | 394.049 | 415.376 | 19.059 | 396.317 | 2.268 |
|  | Feb’15 | 408.877 | 377.958 | 392.532 | 18.182 | 388.532 | 10.574 |
| SOUTHCO | Apr’14 | 274.521 | 286.062 | 275.008 | 0 | 275.008 | -11.054 |
|  | May’14 | 283.671 | 291.135 | 278.532 | 0 | 278.532 | -12.603 |
|  | June’14 | 274.521 | 264.148 | 269.739 | 0 | 269.739 | 5.591 |
|  | July’14 | 283.671 | 252.704 | 265.791 | 0 | 265.791 | 13.087 |
|  | Aug’14 | 283.671 | 267.643 | 277.861 | 0 | 277.861 | 10.218 |
|  | Sept’14 | 274.521 | 264.708 | 272.043 | 0 | 272.043 | 7.335 |
|  | Oct’14 | 283.671 | 260.148 | 259.509 | 0 | 259.509 | -0.639 |
|  | Nov’14 | 274.521 | 262.625 | 261.393 | 0 | 261.393 | -1.232 |
|  | Dec’14 | 283.671 | 254.595 | 257.783 | 0 | 253.783 | -0.812 |
|  | Jan’15 | 283.671 | 251.594 | 257.745 | 0 | 257.745 | 6.151 |
|  | Feb’15 | 256.219 | 228.697 | 239.717 | 0 | 239.717 | 11.02 |

*The above figures are as per EBC data. Energy drawal by SOUTHCO are excluding of energy consumed by NALCO at Damanjodi and IMFA at Theruvali.

Members may please discuss

PART C – issues raised in 107th OCC meeting of ERPC

C1: DR, EL, PLCC and Reactor status installed in Eastern Region.

In 106th OCC, Powergrid agreed to restore and maintain the PLCC system at both ends (its own end as well as the constituent end) of a line wherein the other ends are not being maintained by respective constituents for some reasons or others. It was decided that the cost of restoration and maintenance of PLCC system at such (constituent) ends of the line will be borne by the respective constituents. In addition to this the constituents also agreed to extend all possible support to Powergrid in carrying out the above work.

This was already intimated to C.G.M. (O&M) / G.M. (Telecom) by SLDC. Action taken in this regard may be updated. List of such PLCC equipments to be handed over to PGCIL has been intimated to ERPC by GM (Telecom).

In the last meeting, CGM (O&M) stated that commissioning of EL at Bidanasi has been done. Commissioning of EL at 11 Nos. of S/Ss shall be completed by March 2015. Data from 400 kV Mendhasal and Meramundali S/Ss can be retrieved from the numerical relays. OHPC stated that EL at Indravati PH is functioning and need to be synchronized with GPS. It was decided that OHPC may take action for installation of EL at their Balimela, Rengali and Upper Kolab PHs. This has also been discussed in the 106th OCC meeting of ERPC.

CGM (O&M) / G.M. (Telecom) / OHPC may please deliberate.

C2: 220 kV inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG) S/s

400/220 kV, 2X 315 MVA S/S at Bolangir has been established by Powergrid as part of  ISTS system & the following 220 kV interconnecting lines was envisaged to be established by OPTCL:

CGM (Construction) stated that 220 kV Bolangir-Bolangir (PG) line, which is a part of 220 kV Bolangir–Kesinga D/C line with one ckt LILO at Bolangir(PG) may be delayed due to land dispute issue raised by IDCO. The schedule of commissioning of the line is as follows:

- LILO of OPTCL’s Burla-Bolangir line (One ckt) at Bolangir (PG): March 2015

- 220 kV Bolangir –Kesinga D/C line with one ckt LILO at Bolangir(PG): March’15

CGM (Const.) / CGM (O&M) may please update the status.

C3: Status of “Third Party Protection Audit”

It was deliberated in the OCC that work order has been placed to CPRI, Bangalore for conducting protection audit at Meramundali, Budhipadar, Theruvali & Jaynagar sub-stations.

OPTCL has furnished the requisite data in respect of Tarkera grid sub-station for 2nd third party protection audit. Data for other sub-stations such as Mendhasal & Joda need to be furnished by 31st March 2015. OPTCL may suggest for inclusion of Balasore sub-station in place of Joda and intimate ERPC.

CGM (O&M) may please update the status.

C4: High voltage problem at 400kV Jeypore-OPTCL Substation—OPTCL

In the last meeting it was decided that OHPC shall conduct harmonic study in coordination with OPTCL. Gridco shall send a proposal to CEA Standing Committee for elimination of back to back DC.

OPTCL shall examine for filing Petition before the CERC for not maintaining the bus Voltage at Jeypore (PG) by POWERGRID, as per CEA standard.

In the 107th OCC meeting of ERPC, PGCIL informed that they will install reactor at Jeypore PG within June-2015.

CGM (O&M) / CGM (RT&C) / GRIDCO / OHPC / SLDC may deliberate.

High Voltage at Meramundali sub-station:

In the last meeting, it was decided that SLDC shall monitor the VAr injection by M/s JSPL and M/s BSL on real time basis at Meramundali grid sub-station. OPTCL has already installed 2 X 50 MVAr bus reactor at Meramundali. The 80MVAr line reactor installed in 400kV Angul circuit is out of service due to bursting of LA. However, the Voltage profile at Meramindali has improved after commissioning of the reactor.

CGM (O&M) / CGM (RT&C) / GRIDCO / OHPC / SLDC may deliberate.

C5: Pollution mapping for Eastern Region

In the last meeting, CGM (O&M) stated that major numbers of locations belongs to SOUTHCO. SOUTHCO is not taking initiative for hanging of insulators, even after OPTCL agreed to provide insulators. SOUTHCO may expedite the matter and complete all locations before next PSOC meeting. No information from SOUTHCO is received till date in this regard.

OPTCL / SOUTHCO may please deliberate.

C6: Certification through BIS as per IS 18001:2007 to all generating / transmission units.

In the last meeting CGM (O&M) stated that BIS has not responded yet. However, BIS will be reminded again.

CGM (O&M) may please deliberate the status.

C7: Mock Black start exercises in Eastern Region–ERLDC

The mock black start exercise for Upper Kolab, Balimela & Rengali  HEP is scheduled to be carried out by end of this month.

Members may please note.

C8: Performance of UFR.

It was decided in the 105th OCC meeting of ERPC that constituents should check the UFR enunciation & PT fuse and thereby certify on monthly basis that UFRs are in service.

Further, it was decided to monitor the quantum of load connected to the UFR and constituents are to submit, on quarterly basis, maximum and average load quantum of each feeder with UFRs connected.

The certificate for the month of February 2015 is yet to be furnished by OPTCL which has been discussed in the 107th OCC meeting of ERPC.

CGM (O&M) may please deliberate.

C9: Proposal for review of Power Demand Order (PDO) condition for HVDC Gazuwaka poles, in view of repeated tripping in south Odisha.

ERLDC had made a presentation on the existing and proposed PDOs at HVDC Gazuwaka poles and sought views of OPTCL for implementation in the 106th OCC meeting of ERPC. The proposal has been mailed to CGM (O&M) for views. CGM (O&M) may forward his views directly to ERPC.

CGM (O&M) may please deliberate.

C10: Allocation of Power

ERLDC had made a presentation on the existing and proposed PDOs at HVDC Gazuwaka poles

PART-D – Operational Issues

D1: Non-compliance of drawal schedule by DISCOMs

Non compliance of drawal schedule messages issued to Discoms during the month of February 2015 is as tabled.

| Sl. No | Name of Discom | No. of message issued | Over drawal (MU) |
| --- | --- | --- | --- |
| 1 | CESU | 15 | 47.632 |
| 2 | WESCO | 12 | 25.529 |
| 3 | NESCO | 21 | 10.574 |
| 4 | SOUTHCO | 15 | 11.020 |
|  | Total | 63 | 94.755 |

All the Discoms are requested to predict their drawal in a realistic manner to avoid over drawal / under drawal. Frequent revision of drawal schedule may be avoided as for as possible.

Discoms may please deliberate.

D2: Availability of data of real time power flow of feeders covered under Under-frequency Load shedding scheme (UFLS) and lower relief expected to obtained in real time system operation

In the last meeting GM (Telcom.) stated that the performance BG submitted by the Firm “M/s Industrial Control” was not in line with OPTCL requirement. The firm has been asked to comply with.

G.M. (Telecom) / Sr. G.M. (CPC) may please update the status.

D3: Reporting of Sequence of Events (SoE) at Meramundali S/S

In the last meeting GM (Telcom) stated that E&MR wing have installed separate TB for CMR. Telecom shall install CMR by 2nd week of March’15. SLDC stated that the garbage data need to be blocked.

G.M. (Telecom) / Sr. G.M. (O&M)-II, Meramundali may deliberate.

D4: Repeated damage of Lightning Arrester at Meramundali Sub-station.

It is observed that LA installed at Meramundali sub-station are being damaged frequently causing tripping of important transmission elements which needs to be investigated.

In the last meeting GM (O&M) stated that due to persistence high Voltage, the L.As at Meramundali are getting stressed. The magnitude of 3rd harmonic at Meramundali and Mendhasal are ok. The old LAs need to be replaced.

Failure of L.A. may also be due to increase in pollution level causing flashover under operating Voltage. The analysis indicating the reasons of failure is annexed herewith for further examination and remedial measures by O&M. It is also suggested to conduct performance testing of LAs & other equipment to prevent from failure.

CGM (O&M) may please deliberate.

D5: Reporting of major incidents.

In the last meeting, GM (O&M) stated that Electromagnetic Relays at Narendrapur and Bhanjanagar S/Ss and need to be replaced. E&MR wing of respective circles are requested to create awareness between the Shift Engineers for study of the relay indications for proper reporting.

CGM (O&M) may please deliberate.

D6: Anti theft charging of 400 kV lines emanating from Meramundali.

It is noticed that 400kV long transmission lines (under construction) emanating from Meramundali sub-station have been charged at 400kV voltage level to prevent theft of conductor. Idle charging of these lines causes over voltage at Meramundali sub-station as well as injection of reactive power to ER grid for which GRIDCO is paying reactive energy charges. Further, tripping of the said lines leads to tripping of other 400kV lines also. Subsequent charging of the 400kV lines calls for obtaining charging code from ERLDC, which takes more time for restoration. It is suggested to make antitheft charging at a lower voltage level (220kV / 132kV).

Members may discuss.

D7: Levy of Reactive Energy Charges due to injection of VAR to the grid.

It is noticed that GRIDCO is the only constituent in ER, liable to pay Reactive Energy charges due to injection of reactive power to the pool at the following inter connection point for the period from 23.02.2015 to 01.03.2015.

- 400kV Indravati Indravati PG

- 400kV Meramundali- Angul PG D/C

- 220kV Rengali – Rengali PG D/C

- 132 kV Baripada PG - Rairangpur

Members may discuss.

D8: Prolonged outage of transmission elements and tentative revival dates

| Sl.No | Name of transmission element | Reason of outage | Probable date of revival |
| --- | --- | --- | --- |
| 1 | 220 kV Jayanagar-Theruvali ckt-III Breaker | Breaker defunct | Breaker received. March 2015 |
| 2 | 220/132 kV, 100 MVA Auto-II at Duburi | After inspection by repairer, date can be ascertained | Can be ascertained after inspection. |
| 3 | 220/132 kV, 100 MVA Auto-II at Joda | -do- | -do- |
| 4 | 220/132 kV, 100 MVA Auto at Bolangir (new) | Replacement of 100 MVA Auto by 160 MVA under progress. | 5th March 2015 |

C.G.M. (O&M) may please update the status.

D9: Communication issues

- Installation of communication equipment by CGPs / Industries.

The status of data communication from CGPs as deliberated in the last meeting is as follows

| Sl. No | Name of CGP | Present status |
| --- | --- | --- |
| 1 | M/s Sri Ganesh Metalicks Ltd. | PLCC / SCADA not established. M/S Sri Ganesh proposed for communication through wireless communication mode. They have been permitted for testing. No progress thereafter. |
| 2 | M/s IFFCO, Paradeep | Work has been awarded to M/s Bharat Kumar Sahoo. Outdoor commissioning work is expected to be completed by a week time. Requisition for line shutdown has made for 24th & 25th February’15 for the purpose. |
| 3 | M/s MSP Mettalicks | PLCC / RTU installed. Database has already been prepared by OPTCL. Final RTU integration with OPTCL system by the vendor is awaited. |
| 4 | M/s NINL, Duburi | M/s NINL has requested for Scheme, BOQ for PLCC / SCADA, which has been forwarded by OPTCL. |
| 5 | M/s Adhunik Metallics | PLCC & RTU installed. Database has prepared by OPTCL. Commissioning of RTU is yet to be done. |
| 6 | M/s Rohit Ferrotech | PLCC established and inspection by Telecom Engineers completed. Data base has already been prepared by OPTCL. |
| 7 | M/s VAL, Jharsuguda | No isolator status is available. MW/ MVAR not available for Sterlite 1/2 line, station transformer / Smelter. CBs of Bus coupler data, Bus-1 kV/Hz are not available. As per MOM between OPTCL & Sesa Sterlite, Jharsuguda dtd 22.09.2014, provision for telemetry data will be extended within 6 months.(March,2015) |

All the CGPs have agreed to establish data communication system by March 2015 in the meeting held on 27th November 2014.

GCC / GM (Telcom.) may please deliberate

- Availability of Tap position of 400kV ICTs at Mendhasal.

Tap position data for Mendhasal ICTs are not available for display through SCADA.

GM (Telecom) stated that PCB for ICT –II has already been installed and working. PCB for ICT-I will be installed after availing of line shutdown.

It is also noticed that tap position of Meramundali ICTS are not available for SCADA display.

CGM (O&M) / G.M. (Telecom) may update.

- Availability of data at SLDC.

The data for the following elements are not available for SCADA display.

- Power flow through 132 kV Paradeep- Jagatsinghpur ckt.

- Power flow through 132 kV Jajpur Road- Anandpur ckt.

- Machhakund generation data

- JSPL (Angul) generation data

G.M. (Telecom) may please deliberate.

- Integration of new element.

M/s SSL-SEZ became a consumer of WESCO with effect from 20.03.2015 and importing power through intra State open access from its CGP at Jharsuguda as well as from other utility. The drawal of SSL-SEZ needs to be integrated to SCADA to ascertain WESCO drawal and State demand on real time basis. Telecom may explore for integration of SSL-SEZ drawal and display in the VPS of SLDC control room.

G.M. (Telecom) may please deliberate.

D10: Display of dashboard data.

On 24.02.2015, IT representative presented a demo to all Discoms after the PSOC meeting regarding display of Dash board data in the new format and invited feedback from all Discoms, which is yet to be received. G.M. (Telecom) shall nominate a nodal officer to receive the complaint of Discoms on real time basis for taking necessary action.

DISCOM / CGM (IT) / G.M. (Telecom) may please deliberate.

D11: DISCOM Issues

CESU:

- Deliberation of CESU was not properly recorded in minutes of 83rd meeting.

- Display of incorrect dashboard data leading to wrong forecast of day-ahead drawal.

- Inability of CESU representative to check the data by verifying from the field.

- Disconnection of feeders without consent of CESU.

- Non-co-operation of SLDC to CESU executives deployed at SLDC.

- Non-response of CGM (O&M) for meeting with CESU.

- Dispute of power drawal through Pallahara feeder is yet to be resolved.

- Suo-motu implementation of deviation settlement mechanism by SLDC.

CGM (IT) / GRIDCO / SLDC / OPTCL may please deliberate.

SOUTHCO:

- Dashboard data in the new format is yet to be displayed.

- Soft copy of meter data is not being received by SOUTHCO.

- Hand tripping of 33 kV feeders from Grid on request by DSOCC of SOUTHCO to avoid over drawal.

PART E: OPERATIONAL PLANNING

E1:  Commissioning status of New Transmission elements.

As deliberated in lat meeting the status of commissioning of new transmission elements is as follows:

| Sl. No | Details of transmission element | Present Status |
| --- | --- | --- |
| 1 | Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line | Work has already been started. Expected to be completed by June 2015. |
| 2 | Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt | Line is ready and shall be charged after commissioning of 3rd ICT at Mendhasal for which work order / PO issued. (October-2015) |
| 3 | Commissioning of 400 kV Ib-Meramundali D/C line. | 400kV SSEL-Meramundali line has been idle charged from SSEL end. Due to theft of conductor line could not be charged. Expected to be charged by end of March’2015. |
| 4 | Commissioning of 400 kV Duburi-Meramundali D/C line. | Work is in progress after disposal of Case. Expected by the end of March 2015. |
| 5 | Commissioning of 220 kV Bidanasi-Cuttack line | Work in progress and expected to be completed by June 2015. |
| 6 | Commissioning of 220/132 kV Cuttack S/S | Work in progress and expected to be completed by June 2015. |
| 7 | Commissioning of 132 kV Baripada (PG)-Jaleswar line | Work has already been started, which will be completed by December 2015. |
| 8 | Commissioning of 220/132 kV Kesinga S/S | Work under progress. Expected by September 2015. |
| 9 | Connectivity to Keonjhar PG | Proposal is mooted to be placed in the BoD meeting for connecting the proposed 220 / 33 kV Keonjhar S/S and with Turumunga S/S through 2 Nos. 220 kV ckts each.. |
| 10 | LILO of 220 kV Burla - Bolangir line (one ckt) at Bolangir(PG) | Work awarded. Expected to be completed by March, 2015 |
| 11 | 220 kV Bolangir –Kesinga D/C line and LILO of one ckt at Bolangir(PG). | 220kV Bolangir – Kesinga D/C line is under construction. It is proposed to connect Bolangir (PG) through LILO arrangement of one ckt. (may be delayed due to land dispute with IDCO) |

[Action: CGM (Construction)]

Status of Discom’s action plan for power drawal from the S/Ss expected to be commissioned in near future.

| Sl. No | Name of the sub-station | Probable month of commissioning | Name of DISCOM | Action taken by Discoms |
| --- | --- | --- | --- | --- |
| 1 | 132/33kV, 2x20 MVA Banki | January’15 | CESU | 33 kV feeder work completed. |
| 2 | 132/33kV, 2x20 MVA Konark | Mar’15 | CESU | Line existing |
| 3 | 132/33kV, 2x20 MVA Samuka beach | Mar’15 | CESU | L&T has taken up |
| 4 | 132/33kV, 2x20 MVA Khajuriakota | June’15 | CESU |  |
| 5 | 132/33kV, 2x40 MVA Sarasmal | March’15 | WESCO |  |
| 6 | 132/33kV, 2x40 MVA Kalunga | March’15 | WESCO |  |
| 7 | 220/33kV, 2x20 MVA Banei | Dec’15 | WESCO |  |
| 8 | 132/33kV, 2x20 MVA Boud | January’15 | SOUTHCO | 33 kV Boudh feeder completed. Purunapatna feeder under progress |
| 9 | 132/33kV, 2x12.5 MVA Dabugaon | March’15 | SOUTHCO | 33 kV Dabugaon and Papadahandi feeder completed |
| 10 | 132/33kV, 2x12.5 MVA Umerkote | Mar’15 | SOUTHCO | Requisition for funds placed |
| 11 | 132/33kV, 2x20 MVA Nawapara | January’15 | WESCO | 33 kV feeder work completed. |
| 12 | 132/33kV, 2x20 MVA Padmapur | June’15 | WESCO |  |
| 13 | 132/33kV, 2x20 MVA Udala | Dec-15 | NESCO | Line existing |
| 14 | 132/33kV, 2x20 MVA Somanathpur | March’15 | NESCO |  |

As decided in the last meeting, CESU stated that action is being taken for construction of 33/0.4 kV S/S at Mendhasal to avail power supply for Mendhasal area.

All DISCOMS may update the status.

E2: Installation of Energy Metering at Hydro / Traction & Solar projects.

In the last meeting it was deliberated by OHPC that ABT compliance energy meters have been installed at all OHPC stations except Indravati and was agreed to provide the required assistance to M/s Secure Meters for installation of meters at Indravati PH. Discoms are requested to ask railway authority for change of CT / PT and identify the space for meter installation. It was decided that, from 1st March OPTCL shall take meter reading from those meters. Installation of meters at Indravati shall be completed prior to 1st March.

GRIDCO may forward the meter details and the billing logic in respect of all hydro power stations to SLDC to incorporate in the ERP. If required, the PPA may be modified.

CGM (O&M)may update the status / OHPC / WESCO may please deliberate.

E3: Metering issue of TTPS.

In the last meeting Director (Commercial) Director (Commercial) stated that 1st round discussion has been done. The matter shall be resolved soon. GRIDCO shall forward the meter details and the billing logic to SLDC for TTPS to incorporate in the ERP.

GRIDCO / TTPS may please update.

E4: Construction of 220 kV Tarkera-RSP 2nd DC line.

In the last meeting, CGM (O&M) stated that a system study is required for construction of 220 kV 2nd DC line for providing additional quantum of power to RSP. CGM (Construction) shall write a letter to CGM (O&M) for system study.

CGM (Const.) / RSP may please deliberate.

E5: Shifting of 33 kV line from Balasore Grid S/S yard to facilitate separation of Tfr and Balasore Alloy bays.

In the last meeting, NESCO stated that estimate for shifting of 33 kV line from Balasore Switchyard is under process. CGM (O&M) stated that NESCO has to expedite the work, as it is very much delayed.

NESCO may please deliberate.

E6: Major Events in the month of February’15

There is no report of major events received during February 2015

E7: Important Grid Incidences during the month of February’15.

Important incidents occurred during the month of February’15 are as detailed.

- On 02.02.2015 at 12:43 hrs 220 kV Theruvali-Indravati Ckt-III tripped at both ends on D/P, ‘Y’ ph, E/F, Zn-I relay indication. At 13:00 hrs while charging the above feeder it tripped pulling 220 kV  Indravati Ckt-I & II, 220 kV Laxmipur Ckt-II , 220/132 kV, 100 MVA, Auto-I & II  at Theruvali S/S. On investigation it was found that ‘Y’ ph conductor of  220 kV Theruvali-Indravati Ckt-III snapped.

- On 10.02.15 at 16:25 hrs

BALIMELA

Heavy jerk was noticed at Balimela Power House and as a precautionary measure all running unit (#2 & #3) of Balimela hand tripped. 220 kV Jayanagar-Balimela ckt- 1 & 3 tripped.

UPPER KOLAB

220 kV Jayanagar-Upper Kolab ckt 1 & 2 tripped on Over Voltage at Upper Kolab end.

UPPER INDRAVATI

Heavy frequency oscillation between 44 to 56 Hz and over Voltage noticed at Indravati PH followed by tripping of 400 kV Indravati-Indravati PG ckt and ICT-I & II. The only running unit of Indravati PH was hand tripped.

THERUVALI

Unbalance system Voltage was observed and 220 kV Voltage at Theruvali rose to the tune of 287 kV. Auto transformers at Theruvali hand tripped due to abnormal sound. 220 kV Theruvali-Laxmipur Ckt-I tripped at both ends and ckt-II tripped at Laxmipur end only. Simultaneously, Theruvali-Narendrapur Ckt-I tripped at Theruvali end on D/P Zn-I, ‘R’ ph, E/F. 220 kV Theruvali-Bhanjanagar Ckt-I&II tripped at Bhanjanagar end only.

JAYANAGAR

220 kV Jayanagar Laxmipur ckt-II tripped at LAXMIPUR

NARENDRAPUR & MERAMUNDALI

220 kV Narendrapur-Mendhasal Ckt tripped at Narendrapur . 220 kV Bhanjanagar- Meramundali Ckt-I & II tripped at Mertamundali due to burning of pipe bus to isolator jumper of Bjanjanagar ckt-II.

During restoration 220 kV Jaynagar-Theruvali Ckt-II ‘B’ ph LA and 220 kV Theruvali-Laxmipur Ckt-I ‘R’ ph LA were burst at Laxmipur S/S.

- On 19.02.2015 at 22:31hrs, 400 kV Angul Ckt-I , tripped at Meramundali S/S. Simultaneously, 220 kV ICT-I& II also tripped at Meramundali S/S.  On investigation it was found that ‘B’ ph reactor LA of 400 kV Angul Ckt-I burst at Meramundali S/S.

- On 20.02.15 at 14:11 hrs 160 MVA Auto-I at Jaynagar tripped pulling out 100 MVA Auto-II and 132 kV Machhkund feeder at Jaynagar end.  Simultaneously 220 kV Balimela Ckt-I & III, Upper Kolab Ckt-I&II, Jeypore PG Ckt-I &II, Laxmipur Ckt-I &II tripped. On investigation it was found that 132 kV side ‘B’ ph CT of 160 MVA Auto-I burst.

C.G.M. (O&M) may please deliberate.

E8: Outage of major transmission Elements during the month of February’15. (above 10 hrs).

Outage of major transmission elements above 10 hours during the month of February’15 is as detailed.

| Sl No | Transmission lines | Tripping Dt/time | Restoration Dt/time | Reason |
| --- | --- | --- | --- | --- |
| 1 | 220 kV Theruvali-Indravati Ckt-III | 02.02.15 12:43 | 15.02.15 10:44 | ‘Y’ ph conductor snapped between Loc. No-206 & 207 |
| 2 | 400/220 kV , 315 MVA ICT-I at Mendhasal | 04.02.15 17:34 | 05.02.15 04:29 | 400 kV side ‘R’ ph LA burst. |
| 3 | 132 kV Chandaka-Nimapara Ckt | 08.02.15 15:53 | 09.02.15 12:51 | ‘R’ ph insulator damaged at Loc. No-193 |
| 4 | 132 kV Paradeep-IFFCO Ckt-II | 09.02.15 01:25 | 09.02.15 18:56 | ‘R’ ph conductor snapped at Loc. No-30 of Ckt-I |
| 5 | 132 kV Paradeep-IFFCO Ckt-II | 09.02.15 03:32 | 09.02.15 18:56 |  |
| 6 | 220 kV Jaynagar-Laxmipur Ckt-II | 10.02.15 17:12 | 11.02.15 14:50 | ‘B’ ph LA at Laxmipur burst. |
| 7 | 220 kV Theruvali-Laxmipur Ckt-I | 10.02.15 17:51 | 11.02.15 13:01 | ‘R’ ph LA at Laxmipur burst. |
| 8 | 132 kV Paradeep-Jagatsingpur Ckt | 12.02.15 16:26 | 13.02.15 08:10 | Line patrolling was done but no fault found. |

C.G.M. (O&M) may please deliberate.

E9: Review of Outage Program of State Generators / Transmission elements for the month of March & April’15:

Tentative Outage programme for State Generators for the month of March & April’15 are as follows:

| Sl. | Station | Unit | Period | Remarks |
| --- | --- | --- | --- | --- |
| 1 | Burla | # 1 # 6 # 7 | 06.04.15 to 03.08.15 17.02.14 to continue 28.02.15 to 31.03.15 | Capital Maintenance Programming for R, M & U Annual Maintenance |
| 2 | Chiplima | #3 | 15.02.14 to 31.05.15 | Programming for R & M |
| 3 | Balimela | # 1 # 7 | 31.01.13 to continue 02.04.15 to 25.04.15 | Programming for R, M & U Annual Maintenance |
| 4 | Rengali | # 1 # 2 | 15.04.15 to 30.04.15 15.04.15 to 30.04.15 | Governor Rectification Governor Rectification |
| 5 | Upper Kolab | # 1 | 15.04.15 to 28.08.15 | Capital Maintenance |
| 6 | Upper Indravati | # 1 # 2 | 28. 03.15 to 22.04.15 24.04.15 to 18.05.15 | Annual Maintenance Annual Maintenance |

OHPC may deliberate.

E10: Generation Program for the month of March’15.

Generation schedule for the month of March’15 furnished by OHPC are given below.

| Name of Hydro Gen. Station | Generation Programme (MW) | Reservoir Level as on 01.03.14 | Reservoir Level as on 01.03.15 | MDDL | High Flood Reservoir Level |
| --- | --- | --- | --- | --- | --- |
|  | April’15 |  |  |  |  |
| HPS, Burla | 40+30 | 622.52ft | 618.89ft | 590 ft. | 630 ft. |
| Balimela | 80 | 1503.50ft ft | 1501.30ft | 1440 ft. | 1516 ft. |
| Rengali | 80 | 121.70mt 1.78mt mtr mt | 120.43mt mt | 109.72mtr mtr mtr. | 123.5 mtr. |
| U.Kolab | 80 | 854.24mt mt | 854.81mt | 844 mtr mtmtr. | 858 mtr. |
| U.Indravati | 300 | 639.70mt mt | 637.84mt mt | 625mtr mtr mtr. | 642 mtr |
| MKD (O/D) | 30 | 2740.70ft ft | 2735.65ft ft | 2685 ft. | 2750 ft. |
| TOTAL | 640 |  |  |  |  |

OHPC may update.

PART F: OTHER ISSUES

F1:  Members may raise issues, if any.

F2:  Date and Venue of the next (85th) PSOC meeting: