Distribution list

            - The Director (Commercial), Gridco, Bhubaneswar

            - The Director (Operation), OHPC, Bhubaneswar

            - The CGM (O & M), OPTCL, Bhubaneswar

            - The CGM (Const.), OPTCL, Bhubaneswar

            - The CGM, (RT&C), OPTCL, Bhubaneswar

            - The C.G.M. (PP), GRIDCO, Bhubaneswar

            - The CGM (IT), OPTCL, Bhubaneswar

            - The Sr. G.M (C.P), OPTCL, Bhubaneswar

            - The Sr. G.M. (TP&C), OPTCL, Bhubaneswar

            - The Sr. G.M. (CPC), OPTCL, Bhubaneswar

            - The Sr. G.M.(O&M), Zone-I, Narendrapur

            - The Sr. G.M.(O&M), Zone-II, Meramundali

            - The Member Secy., (GCC), OPTCL, Bhubaneswar

            - The C.E.O., CESU, Bhubaneswar

            - The A.O.,WESCO Utility, Burla

            - The A.O., NESCO Utility, Balasore

            - The A.O., SOUTHCO Utility, Berhampur

            - The G.M. (Telecom), OPTCL, Bhubaneswar

            - The Vice President (O), IMFA, Choudwar

            - The D.G.M (Electrical), IbTPS, OPGC, Banharpali

            - The G.M. (O &M), CPP, NALCO, Angul

            - The DGM (O & M), NTPC (TTPS), Talcher

            - The G.M., HINDALCO, Hirakud

            - The D.G.M. (Power Distribution), RSP, Rourkela

            - The D.G.M. (Elect.), JINDAL Stainless Ltd, Duburi

            - The G.M., Vedanta Aluminium Ltd., Jharsuguda

            - The G.M.(Elect.), Bhushan Steel & Power Ltd, Budhipadar

            - The Sr. G.M. (Elect.), Bhusan Steel Limited, Meramundali

            - The S.E., Machhakund

## Odisha Power Transmission Corporation Ltd. Bhubaneswar.

Minutes of 84th PSOC meeting held on 26.03.2015 at PTC, Chandaka

List of participants is at Annexure.

Sr. G.M (Power System) welcomed all the participants to the 84th Power System Operational Coordination meeting and highlighted the system performance during the month of February’2015 and overall power scenario of the State. He also emphasized on the drawal by all the Discoms during the month.

The meeting was chaired by Director (Commercial), GRIDCO.

D.G.M. (SS) took the agenda items for discussion.

The review proceeded as follows:

PART A: CONFIRMATION OF MINUTES

A.1: Confirmation of minutes of 83rd PSOC meeting held on 24.02.2015

The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2014/638(30), dated 10.03.2015 to all the members and also uploaded in the SLDC website. No comment has been received from any of the members.

Deliberation in the meeting

Minutes of 83rd PSOC meeting was confirmed since no comments were received.

PART B : SYSTEM PERFORMANCE

B1: Review of Grid Performance for the month of February’2015.

## (A)  Frequency

It was noticed that, during the month, 57.36% of times the frequency remained in the IEGC band i.e.  49.90Hz - 50.05Hz in comparison to 51.40 % during the month of January’15. The maximum and minimum System frequency during the month of February’15 was 50.35 Hz & 49.68 Hz respectively.

## (B)  Grid demand

Grid demand for the month of February’15 was reviewed. The energy consumption during the month was 1806 MU. The maximum System demand of 3613 MW occurred on 26.02.2015 at 20:00 Hrs and minimum demand of 1979 MW occurred on 12.02.2015 at 16:00 Hrs.

Deliberation in the meeting

It is observed that energy consumption during the month of February’ 15 was decreased by 113 MU, while the peak demand during the month has increased by 149MW from that of January’15. The energy consumption during the month has been increased by 10 MU in comparison to February’14.

(C)  Voltage Profile of important Sub Stations in OPTCL System.

The Voltage profile at different 220 kV buses in OPTCL system during the month of February’15 was reviewed. It is noticed that Jayanagar 220 kV bus have experienced a maximum voltage of 247.56 kV, while minimum Voltage of 201.14 kV was experienced at Paradeep 220 kV bus.

Deliberation in the meeting

Sr. G.M (PS) stated that issue of persisting high voltage at Jayanagar has been raised in the OCC meeting of ERPC. Powergrid has scheduled for installation of additional reactor at Jeypore by June’2015. Replacement of CVT at Bidanasi S/S has been done on 28.02.2015. O&M shall check the CVT at Meramundali.

[Action: CGM (O&M)]

(D) Energy Generation / import during the month of February’15

Energy generation and exchange during the month of February’15 was reviewed. The total quantum of energy drawn from all the generation sources including Central Sector Share and CGP/IPP support during the month was 1806 MU.

(E) Drawal of Machhakund Power

The drawal of Machhakund power during the month of February’15 was 29.411 MU against AP drawal of 29.372 MU

In the last meeting Sr. G.M (O&M), Zone-I stated that bus modification work at Jayanagar S/S is will be taken up after commissioning of Auto at Jayanagar. G.M (Telecom) stated that installation of OPGW equipments at Machhakund and Jayanagar by POWERGRID is expected to be completed by June 2015. After which, Remote Subscriber (RS) phone provision can be made from Jayanagar S/S. Southco Utility stated that around 1.5 MW load has been extended to Akusingh Grid by linking 33/11kV Substation Kumbhar Dhamuni.  Other linking lines as suitable are being taken up.

In the month of March SLDC & GRIDCO officers had been to Machhakund PH to study the present metering arrangement in view of selling of Machhakund share to AP proposed by GRIDCO. It is proposed to divert the metering cubicle from TTPS to Machhakund PH for proper metering.

Deliberation in the meeting

Sr. GM (O&M), Zone-I stated that bus modification work at Jayanagar S/S is will be taken up after charging of Auto at Jayanagar. G.M (Telecom) stated that installation of OPGW equipments at Machhakund and Jayanagar by POWERGRID is expected to be completed by June 2015. After which, Remote Subscriber (RS) phone provision can be made from Jayanagar S/S. Southco Utility stated that around 1.5 MW load has been extended to Akusingh Grid by linking 33/11kv Substation Kumbhar Dhamuni. Other linking lines as suitable are being taken up.

After finalizing TTPS metering issue, diversion of metering cubicle from TTPS to Machhakund shall examined.

[Action:-G.M (Telecom) / Sr.GM (O&M)-I / SOUTHCO Utility]

- Under Frequency Relay operation in OPTCL System during the month of February’15.

There is no UF Relay operation occurred during the month of February’15 as the frequency had never gone beyond 48.5 Hz.

(G) DISCOM Drawal during the month of February’15

The schedule and actual energy drawal by Discoms for the month of February’15 was reviewed.

Deliberation in the meeting

It was noticed that CESU and WESCO Utility have overdrawn substantially to the tune of 47.63 MU and 25.53 MU respectively, while SOUTHCO Utility have overdrawn 11 MU during the month. NESCO Utility has complied the schedule successfully. CESU stated that the drawal data displayed at SLDC is not correct, which lead wrong prediction of day-ahead drawal.  It was decided that SLDC shall monitor the overdraw of DISCOMs and do the needful for compliance of the drawal schedule. The data displayed shall be checked by the Discom representatives and Telecom officers at SLDC.

[Action: All Distribution Utilities, SLDC, Telecom]

PART C – issues of 106th OCC meeting of ERPC

C1: DR, EL, PLCC and Reactor status installed in Eastern Region.

In 106th OCC, Powergrid agreed to restore and maintain the PLCC system at both ends (its own end as well as the constituent end) of a line wherein the other ends are not being maintained by respective constituents for some reasons or others. It was decided that the cost of restoration and maintenance of PLCC system at such (constituent) ends of the line will be borne by the respective constituents. In addition to this the constituents also agreed to extend all possible support to Powergrid in carrying out the above work.

This was already intimated to C.G.M. (O&M) / G.M. (Telecom) by SLDC. Action taken in this regard may be updated. List of such PLCC equipments to be handed over to PGCIL has been intimated to ERPC by GM (Telecom).

In the last meeting, CGM (O&M) stated that commissioning of EL at Bidanasi has been done. Commissioning of EL at 11 Nos. of S/Ss shall be completed by March 2015. Data from 400 kV Mendhasal and Meramundali S/Ss can be retrieved from the numerical relays. OHPC stated that EL at Indravati PH is functioning and need to be synchronized with GPS. It was decided that OHPC may take action for installation of EL at their Balimela, Rengali and Upper Kolab PHs. This has also been discussed in the 106th OCC meeting of ERPC.

Deliberations in the meeting.

D.G.M (Telecom) stated that a list of all such PLCC units to be maintained by POWERGRID has been prepared. The list will be forwarded to ERPC. CGM (O&M) stated that commissioning of EL at 11 Nos. of S/Ss shall be completed by April’ 2015. It was decided that OHPC may take action for installation of  EL at their Balimela, Rengali and Upper Kolab PHs and synchronization of Indravati EL with GPS.

[Action: GM (Telecom.) / OHPC]

C2: 220 kV inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG) S/s

400/220 kV, 2X 315 MVA S/S at Bolangir has been established by Powergrid as part of  ISTS system & the following 220 kV interconnecting lines was envisaged to be established by OPTCL:

Deliberations in the meeting.

It was deliberated that 220 kV Bolangir-Bolangir (PG) line, which is a part of 220 kV Bolangir–Kesinga D/C line with one ckt LILO at Bolangir(PG) may be delayed due to land dispute issue raised by IDCO. The schedule of commissioning of the line is as follows:

- LILO of OPTCL’s Burla-Bolangir line (One ckt) at Bolangir (PG): May 2015

- 220 kV Bolangir –Kesinga D/C line with one ckt. LILO at Bolangir(PG): Land dispute.

[Action CGM (O&M) / CGM (Const)]

C3: Status of “Third Party Protection Audit”

It was deliberated in the OCC that work order has been placed to CPRI, Bangalore for conducting protection audit at Meramundali, Budhipadar, Theruvali & Jaynagar sub-stations.

OPTCL has furnished the requisite data in respect of Tarkera grid sub-station for 2nd third party protection audit. Data for other sub-stations such as Mendhasal & Joda need to be furnished by 31st March 2015. OPTCL may suggest for inclusion of Balasore sub-station in place of Joda and intimate ERPC.

Deliberations in the meeting.

CGM (O&M) stated that data for all S/Ss have been furnished to CPRI. Inclusion of Balasore sub-station in place of Joda shall be proposed.

[Action: C.G.M. (O&M)]

C4: High voltage problem at 400kV Jeypore-OPTCL Substation—OPTCL

In the last meeting it was decided that OHPC shall conduct harmonic study in coordination with OPTCL. Gridco shall send a proposal to CEA Standing Committee for elimination of back to back DC.

OPTCL shall examine for filing Petition before the CERC for not maintaining the bus Voltage at Jeypore (PG) by POWERGRID, as per CEA standard.

In the 107th OCC meeting of ERPC, PGCIL informed that they will install reactor at Jeypore PG by June-2015.

High Voltage at Meramundali sub-station:

In the last meeting, it was decided that SLDC shall monitor the VAr injection by M/s JSPL and M/s BSL on real time basis at Meramundali grid sub-station. OPTCL has already installed 2 X 50 MVAr bus reactor at Meramundali. The 80MVAr line reactor installed in 400kV Angul circuit is out of service due to bursting of LA. However, the Voltage profile at Meramundali has improved after commissioning of the reactor.

Deliberations in the meeting.

OHPC stated that offer for supply of Power Quality Analyzer has been invited. Sr. GM (PS) stated that high Voltage problem at Meramundali has been addressed after commissioning of reactor at Meramundali.  In the OCC meeting of ERPC, PGCIL informed that they will install reactor at Jeypore PG by June-2015. SLDC shall monitor the VAr injection by M/s BSL and M/s JSPL on real time basis.

[Action: SLDC / OHPC]

C5: Pollution mapping for Eastern Region

In the last meeting, CGM (O&M) stated that major numbers of locations belongs to SOUTHCO Utility. SOUTHCO Utility is not taking initiative for hanging of insulators, even after OPTCL agreed to provide insulators. SOUTHCO Utility may expedite the matter and complete all locations before next PSOC meeting. No information from SOUTHCO Utility is received till date in this regard.

Deliberations in the meeting.

Southco Utility stated that out of 26 Nos of locations hanging of insulators for 5 Nos have been completed. The remaining locations shall be completed soon. Other Distribution utilities shall take necessary action for hanging of insulators at their specified locations.

[Action: Southco Utility]

C6: Certification through BIS as per IS 18001:2007 to all generating / transmission units.

In the last meeting CGM (O&M) stated that BIS has not responded yet. However, BIS will be reminded again.

Deliberations in the meeting.

CGM (O&M) stated that BIS will be once again reminded.

[Action : CGM (O&M)]

C7: Mock Black start exercises in Eastern Region–ERLDC

The mock black start exercise for Upper Kolab, Balimela & Rengali  HEP is scheduled to be carried out by end of this month.

Deliberations in the meeting.

SLDC stated that mock black start exercise for Rengali PH has been done. Balimela PH was not conducted the exercise due to communication failure, which will be repeated.

[Action: OHPC / SLDC]

C8: Performance of UFR.

It was decided in the 105th OCC meeting of ERPC that constituents should check the UFR enunciation & PT fuse and thereby certify on monthly basis that UFRs are in service.

Further, it was decided to monitor the quantum of load connected to the UFR and constituents are to submit, on quarterly basis, maximum and average load quantum of each feeder with UFRs connected.

The certificate for the month of February 2015 is yet to be furnished by OPTCL which has been discussed in the 107th OCC meeting of ERPC.

Deliberations in the meeting.

It was decided that CGM (O&M) shall furnish the certificate in respect of healthiness of UFR scheme each month.

[Action: CGM (O&M)]

C9: Proposal for review of Power Demand Order (PDO) condition for HVDC Gazuwaka poles, in view of repeated tripping in south Odisha.

ERLDC had made a presentation on the existing and proposed PDOs at HVDC Gazuwaka poles and sought views of OPTCL for implementation in the 106th OCC meeting of ERPC. The proposal has been mailed to CGM (O&M) for views. CGM (O&M) may forward his views directly to ERPC.

Deliberations in the meeting.

It was decided that CGM (O&M) shall examine the scheme and forward OPTCL’s view to ERPC.

[Action : CGM (O&M)]

PART-D – Operational Issues

D1: Non-compliance of drawal schedule by DISCOMs

Non compliance of drawal schedule messages issued to Discoms during the month of February’15 was reviewed. Maximum 21 numbers of such messages were issued to NESCO Utility followed by 15 Nos. each to WESCO Utility and Southco Utility and 12 Nos to NESCO Utility. Total over drawal by all DISCOM utility were 80.5 MU during the month.

Deliberations in the meeting.

It was decided that SLDC shall coordinate with the officers of Distribution utility deployed in the control room before issuing non-compliance message and allow one block time, failing which the message shall be sent to the defaulting Distribution utility. All the Discoms were requested to predict their drawal in a realistic manner to avoid over drawal / under drawal. Frequent revision of drawal schedule may be avoided as far as possible.

[Action: All Distribution Utility]

D2: Availability of data of real time power flow of feeders covered under Under-frequency Load shedding scheme (UFLS) and lower relief expected to obtained in real time system operation

In the last meeting GM (Telecom.) stated that the performance BG submitted by the Firm “M/s Industrial Control” was not in line with OPTCL requirement. The firm has been asked to comply with.

Deliberations in the meeting.

DGM (Telecom) stated that the delivery date is 06.04.2015. The firm has requested to accept DD in place of CBG. However the firm is yet to submit offer for inspection.

[Action: GM (Telecom)]

D3: Reporting of Sequence of Events (SoE) at Meramundali S/S

In the last meeting GM (Telecom) stated that E&MR wing have installed separate TB for CMR. Telecom shall install CMR by 2nd week of March’15. SLDC stated that the garbage data need to be blocked.

Deliberations in the meeting.

DGM (Telecom) stated that the CMR has been installed. There is no garbage data.

[Action: Sr. G.M (O&M), Zone-II /GM (Telecom)]

D4: Repeated damage of Lightning Arrester at Meramundali Sub-station.

It is observed that LA installed at Meramundali sub-station are being damaged frequently causing tripping of important transmission elements which needs to be investigated.

In the last meeting GM (O&M) stated that due to persistence high Voltage, the L.As at Meramundali are getting stressed. The magnitude of 3rd harmonic at Meramundali and Mendhasal are ok. The old LAs need to be replaced.

Failure of L.A. may also be due to increase in pollution level causing flashover under operating Voltage. The analysis indicating the reasons of failure is annexed herewith for further examination and remedial measures by O&M. It is also suggested to conduct performance testing of LAs & other equipment to prevent from failure.

Deliberations in the meeting.

GM (O&M) stated that, the failed LA s at Meramundali and Mendhasal S/S are of CGL make and 10-12 years old. However, O&M shall write to CGL regarding the failure of LAs.

D5: Reporting of major incidents.

In the last meeting, GM (O&M) stated that Electromagnetic Relays at Narendrapur and Bhanjanagar S/Ss and need to be replaced. E&MR wing of respective circles are requested to create awareness between the Shift Engineers for study of the relay indications for proper reporting.

Deliberations in the meeting.

GM (O&M) stated that Electromagnetic Relays at Narendrapur and Bhanjanagar shall be replaced by 15th April’2015.

[Action: CGM (O&M)]

D6: Anti theft charging of 400 kV lines emanating from Meramundali.

It is noticed that 400kV long transmission lines (under construction) emanating from Meramundali sub-station have been charged at 400kV voltage level to prevent theft of conductor. Idle charging of these lines causes over voltage at Meramundali sub-station as well as injection of reactive power to ER grid for which GRIDCO is paying reactive energy charges. Further, tripping of the said lines leads to tripping of other 400kV lines also. Subsequent charging of the 400kV lines calls for obtaining charging code from ERLDC, which takes more time for restoration. It is suggested to make antitheft charging at a lower voltage level (220kV / 132kV).

Deliberations in the meeting.

CGM (O&M) stated that Voltage level for anti theft charging of 400 kV lines emanating from Meramundali S/S have already been changed to 220 kV.

D7: Levy of Reactive Energy Charges due to injection of VAR to the grid.

It is noticed that GRIDCO is the only constituent in ER, liable to pay Reactive Energy charges due to injection of reactive power to the pool at the following inter connection point for the period from 23.02.2015 to 01.03.2015.

- 400kV Indravati Indravati PG

- 400kV Meramundali- Angul PG D/C

- 220kV Rengali – Rengali PG D/C

- 132 kV Baripada PG - Rairangpur

Deliberations in the meeting.

GM (O&M) stated that, the reactive power flow at both the ends of transmission line need to be compared to ascertain the VAr injection.  OPTCL /SLDC shall compare such VAr flow and confirm whether the line itself is generating VAr and do the needful.

[Action: O&M / SLDC]

D8: Prolonged outage of transmission elements and tentative revival dates

Deliberations in the meeting

The updated revival / tentative revival of prolonged outage of transmission elements are as detailed.

| Sl.No | Name of transmission element | Reason of outage | Probable date of revival |
| --- | --- | --- | --- |
| 1 | 220 kV Jayanagar-Theruvali ckt-III Breaker | Breaker defunct | Breaker received. May 2015 |
| 2 | 220/132 kV, 100 MVA Auto-II at Duburi | After inspection by repairer, date can be ascertained | Can be ascertained after inspection. |
| 3 | 220/132 kV, 100 MVA Auto-II at Joda | -do- | Rectified and charged on 26.03.15 |
| 4 | 220/132 kV, 100 MVA Auto at Bolangir (new) | Replacement of 100 MVA Auto by 160 MVA under progress. | Charged on 03.03.15 |

[Action: CGM (O&M)]

D9: Communication issues

- Installation of communication equipment by CGPs / Industries.

The status of data communication from CGPs as deliberated is as follows

| Sl. No | Name of CGP | Present status |
| --- | --- | --- |
| 1 | M/s Sri Ganesh Metalicks Ltd. | PLCC / SCADA not established. M/S Sri Ganesh proposed for communication through wireless communication mode. They have been permitted for testing. No progress thereafter. |
| 2 | M/s IFFCO, Paradeep | Work has been awarded to M/s Bharat Kumar Sahoo. Outdoor commissioning work is completed. Testing of DPLC is in progress. |
| 3 | M/s MSP Mettalicks | PLCC / RTU installed. Database has already been prepared by OPTCL. Final RTU integration with OPTCL system by the vendor is awaited. |
| 4 | M/s NINL, Duburi | M/s NINL has requested for Scheme, BOQ for PLCC / SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. |
| 5 | M/s Adhunik Metallics | PLCC & RTU installed. Database has prepared by OPTCL. Commissioning of RTU is yet to be done. |
| 6 | M/s Rohit Ferrotech | PLCC established and inspection by Telecom Engineers completed. Data base has already been prepared by OPTCL. |
| 7 | M/s VAL, Jharsuguda | No isolator status is available. MW/ MVAR not available for Sterlite 1/2 line, station transformer / Smelter. CBs of Bus coupler data, Bus-1 kV/Hz are not available. As per MOM between OPTCL & Sesa Sterlite, Jharsuguda dtd 22.09.2014, provision for telemetry data will be extended within 6 months.(March,2015) |

Sr. G.M (CP) / Member Secretary, GCC stated that after receiving the updated information from Telecom, a meeting shall be convened with all such defaulting CGPs by the GCC.

[Action: GM (Telecom) / Sr. G.M (CP)]

- Availability of Tap position of 400kV ICTs at Mendhasal.

Tap position data for Mendhasal ICTs are not available for display through SCADA.

GM (Telecom) stated that PCB for ICT –II has already been installed and working. PCB for ICT-I will be installed after availing of line shutdown.

It is also noticed that tap position of Meramundali ICTS are not available for SCADA display.

Deliberations in the meeting

DGM (Telecom) stated that Tap position indicator (TPC 2000) have already installed and integrated with RTU for both the ICTs at Mendhasal. The same will be installed for Meramundali as soon as TPC2000 is available.

[Action: GM (Telecom)]

- Availability of data at SLDC.

The data for the following elements are not available for SCADA display.

- Power flow through 132 kV Paradeep- Jagatsinghpur ckt.

- Power flow through 132 kV Jajpur Road- Anandpur ckt.

- Machhakund generation data

- JSPL (Angul) generation data

Deliberations in the meeting

DGM (Telecom) stated that, for item (a) and (b), transducers have been installed and cabling completed. Integration of Transducer with RTU shall be done shortly. For item (c) M/s Chemtrol has been intimated to restore and for item (d) M/s JSPL has been asked to restore its generation data at SLDC soon.

[Action: GM (Telecom)]

- Integration of new element.

M/s SSL-SEZ became a consumer of WESCO Utility with effect from 20.03.2015 and importing power through intra State open access from its CGP at Jharsuguda as well as from other utility. The drawal of SSL-SEZ needs to be integrated to SCADA to ascertain WESCO Utility drawal and State demand on real time basis. Telecom may explore for integration of SSL-SEZ drawal and display in the VPS of SLDC control room.

Deliberations in the meeting

DGM (Telecom) stated that, RTU of M/s SSL-SEZ is reporting to ERLDC. Data at SLDC is being displayed from ERLDC. ERLDC shall be requested to issue of necessary instruction to M/s SSL-SEZ for extending its Smelter data to them, so that the same can be displayed at SLDC. However, the smelter drawal has been made available at SLDC through generalized calculation procedure.

[Action: GM (Telecom)]

D10: Display of dashboard data.

On 24.02.2015, IT representative presented a demo to all Discoms after the PSOC meeting regarding display of Dash board data in the new format and invited feedback from all Discoms, which is yet to be received. G.M. (Telecom) shall nominate a nodal officer to receive the complaint of Discoms on real time basis for taking necessary action.

Deliberations in the meeting

DGM (Telecom) stated that, Mr. P.L Gouda, DM (Telecom.) shall act as nodal officer to receive all complaints of Distribution utilities regarding Dash board problems and rectify thereof. CGM (IT) stated that the newly designed Dashboard is working satisfactorily and the interruption has been reduced considerably. All Distribution Utility were requested to communicate their feedback to CGM (IT) for further modification of the Dashboard display.

[Action: All Distribution Utilities / CGM (IT) / GM (Telecom)]

D11: DISCOM Issues

CESU:

- Mismatch of dashboard data with actual drawal lead to in accurate forecast

- Coordination with CESU representative deployed at SLDC prior to issue of non compliance message.

- Interruption / wrong display are not rectified mostly in the evening hours due to non availability of Telecom staff at SLDC.

- Dispute of power drawal through Pallahara feeder and bilateral issues with other Dist utilities is yet to be resolved.

- Suo-motu implementation of deviation settlement mechanism by SLDC not acceptable to CESU.

Deliberations in the meeting;

As deliberated at item D-10 above, CESU may forward its feedback to CGM (IT) indicating all the problems. However, the displayed data are for monitoring purpose only. CESU may workout the error correction factor to ascertain the actual drawal. Item (2) has already been deliberated at D-1. For Item (3), nodal officer from Telecom, to receive all complaints regarding Dashboard display has been identified. For Item (4), CESU may convene meeting with the WESCO Utility to resolve bilateral issues, failing which the issue may be placed before PSOC meeting. For item (5), SLDC is preparing the Deviation Charge bill as per the Regulation and intimating to OERC also. However, CESU may approach OERC, if aggrieved, for an Order.

[Action: CESU / GM (Telecom)/ CGM (IT)/ SLDC]

SOUTHCO UTILITY:

- Dashboard data in the new format is yet to be displayed.

- Soft copy of meter data is not being received by SOUTHCO Utility.

- Hand tripping of 33 kV feeders from Grid on request by DSOCC of SOUTHCO Utility to avoid over drawal.

Deliberations in the meeting;

Southco Utility was requested to forward their feedback to CGM (IT) regarding the newly designed Dashboard format. Soft copy of meter data is being regularly collected by SOUTHCO Utility officers. Already it was decided to isolate 33 kV feeders from the grid S/Ss as and when requested by Dist. Utility. However Southco Utility may coordinate with the Grid S/Ss for this purpose.

[Action : SOUTHCO Utility]

PART E: OPERATIONAL PLANNING

E1:  Commissioning status of New Transmission elements.

The status of commissioning of new transmission elements is as follows:

| Sl. No | Details of transmission element | Present Status |
| --- | --- | --- |
| 1 | Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line | Work has already been started. Expected to be completed by June 2015. |
| 2 | Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt | Line is ready and shall be charged after commissioning of 3rd ICT at Mendhasal for which work order / PO issued. (October-2015) |
| 3 | Commissioning of 400 kV Ib-Meramundali D/C line. | 400kV SSEL-Meramundali line has been idle charged from SSEL end. Due to theft of conductor line could not be charged. Expected to be charged by end of June’2015. |
| 4 | Commissioning of 400 kV Duburi-Meramundali D/C line. | Work is in progress after disposal of Case. Expected by the end of May 2015. |
| 5 | Commissioning of 220 kV Bidanasi-Cuttack line | Work in progress and expected to be completed by June 2015. |
| 6 | Commissioning of 220/132 kV Cuttack S/S | Work in progress and expected to be completed by June 2015. |
| 7 | Commissioning of 132 kV Baripada (PG)-Jaleswar line | Work has already been started, which will be completed by December 2015. |
| 8 | Commissioning of 220/132 kV Kesinga S/S | Work under progress. Expected by September 2015. |
| 9 | Connectivity to Keonjhar PG | Proposal is mooted to be placed in the BoD meeting for connecting the proposed 220 / 33 kV Keonjhar S/S and with Turumunga S/S through 2 Nos. 220 kV ckts each. |
| 10 | LILO of 220 kV Burla - Bolangir line (one ckt) at Bolangir(PG) | Work awarded. Expected to be completed by June, 2015 |
| 11 | 220 kV Bolangir –Kesinga D/C line and LILO of one ckt at Bolangir(PG). | 220kV Bolangir - Kesinga D/C line is under construction. It is proposed to connect Bolangir (PG) through LILO arrangement of one ckt. (may be delayed due to land dispute with IDCO) |

[Action: CGM (Construction)]

Status of Discom’s action plan for power drawal from the S/Ss expected to be commissioned in near future.

| Sl. No | Name of the sub-station | Probable month of commissioning | Name of DISCOM | Action taken by Discoms |
| --- | --- | --- | --- | --- |
| 1 | 132/33kV, 2x20 MVA Banki | Charged | CESU | 33 kV feeder shall be charged by April’15 |
| 2 | 132/33kV, 2x20 MVA Konark | Apr’15 | CESU | Line existing |
| 3 | 132/33kV, 2x20 MVA Samuka beach | Apr’15 | CESU | Completed by end of Apr’15 |
| 4 | 132/33kV, 2x20 MVA Khajuriakota | June’15 | CESU | 33 kV feeder work shall be completed by June’15 |
| 5 | 132/33kV, 2x40 MVA Sarasmal | Charged | WESCO Utility |  |
| 6 | 132/33kV, 2x40 MVA Kalunga | Apr’15 | WESCO Utility |  |
| 7 | 220/33kV, 2x20 MVA Banei | Dec’15 | WESCO Utility |  |
| 8 | 132/33kV, 2x12.5 MVA Dabugaon | Apr’15 | SOUTHCO Utility | 33 kV Dabugaon and Papadahandi feeder completed |
| 9 | 132/33kV, 2x12.5 MVA Umerkote | Apr’15 | SOUTHCO Utility | 33 kV feeder shall be completed by May’15 |
| 10 | 132/33kV, 2x20 MVA Nawapara | Charged | WESCO Utility | 33 kV feeder work completed. |
| 11 | 132/33kV, 2x20 MVA Padmapur | June’15 | WESCO Utility |  |
| 12 | 132/33kV, 2x20 MVA Udala | Dec-15 | NESCO Utility | Line existing |
| 13 | 132/33kV, 2x20 MVA Somanathpur | May’15 | NESCO Utility | 33 kV feeder existing |

As decided in the last meeting, construction of 33/0.4 kV S/S at Mendhasal to avail power supply for Mendhasal area is yet to be taken up by CESU.

Action: [CGM (Const.) / All Dist. Utility]

E2: Installation of Energy Metering at Hydro / Traction & Solar projects.

In the last meeting it was deliberated by OHPC that ABT compliance energy meters have been installed at all OHPC stations except Indravati and was agreed to provide the required assistance to M/s Secure Meters for installation of meters at Indravati PH. Discoms are requested to ask railway authority for change of CT / PT and identify the space for meter installation. It was decided that, from 1st March OPTCL shall take meter reading from those meters. Installation of meters at Indravati shall be completed prior to 1st March.

GRIDCO may forward the meter details and the billing logic in respect of all hydro power stations to SLDC to incorporate in the ERP. If required, the PPA may be modified.

Deliberations in the meeting

It was decided that, Gridco shall take initiative for revision of PPA clause for billing of OHPC stations from ABT compliance meters.

WESCO Utility shall approach Rly. Authority for installation of required Class of CT & PT at their Bhalulata, Bamara and Chandiposi Traction points.

[Action: Gridco / WESCO Utility / OHPC]

E3: Metering issue of TTPS.

In the last meeting Director (Commercial) Director (Commercial) stated that 1st round discussion has been done. The matter shall be resolved soon. GRIDCO shall forward the meter details and the billing logic to SLDC for TTPS to incorporate in the ERP.

Deliberations in the meeting

It was decided that Gridco shall convene a meeting with TTPS to resolve the issue soon.

[Action: Gridco / TTPS]

E4: Construction of 220 kV Tarkera-RSP 2nd DC line.

In the last meeting, CGM (O&M) stated that a system study is required for construction of 220 kV 2nd DC line for providing additional quantum of power to RSP. CGM (Construction) shall write a letter to CGM (O&M) for system study.

Deliberations in the meeting

The issue could not be discussed due to absence of Construction and RSP representative.

[Action: RSP / CGM (Const)]

E5: Shifting of 33 kV line from Balasore Grid S/S yard to facilitate separation of Tfr and Balasore Alloy bays.

In the last meeting, NESCO Utility stated that estimate for shifting of 33 kV line from Balasore Switchyard is under process. CGM (O&M) stated that NESCO Utility has to expedite the work, as it is very much delayed.

Deliberations in the meeting.

It was decided that, NESCO Utility shall expedite the work.

[Action: NESCO Utility]

E6: Major Events in the month of February’15

There is no report of major events received during February 2015

E7: Important Grid Incidences during the month of February’15.

Important incidents occurred during the month of February’15 were reviewed.

Deliberations in the meeting

GM (O&M) stated that all the S/Ss have already been instructed to furnish reports after due analysis in coordination of E&MR officers.

[Action: C.G.M. (O&M)]

E8: Outage of major transmission Elements during the month of February’15. (Above 10 hrs)

Outage of major transmission elements above 10 hours during the month of February’15 was reviewed.

Deliberations in the meeting

Most of the outages are due to conductor snapping and bursting of LAs. O&M may examine replacement of old LAs to avoid interruption.

[Action: C.G.M. (O&M)]

E9: Review of Outage Program of State Generators / Transmission elements for the month of March & April’15:

Tentative Outage programme for State Generators for the month of March & April’15 are as follows:

| Sl. | Station | Unit | Period | Remarks |
| --- | --- | --- | --- | --- |
| 1 | Burla | # 1 # 6 # 7 | 06.04.15 to 03.08.15 17.02.14 to continue 28.02.15 to 31.03.15 | Capital Maintenance Programming for R, M & U Annual Maintenance |
| 2 | Chiplima | #3 | 15.02.14 to 31.05.15 | Programming for R & M |
| 3 | Balimela | # 1 # 7 | 31.01.13 to continue 02.04.15 to 25.04.15 | Programming for R, M & U Annual Maintenance |
| 4 | Rengali | # 1 # 2 | 15.04.15 to 30.04.15 15.04.15 to 30.04.15 | Governor Rectification Governor Rectification |
| 5 | Upper Kolab | # 1 | 15.04.15 to 28.08.15 | Capital Maintenance |
| 6 | Upper Indravati | # 1 # 2 | 28. 03.15 to 22.04.15 24.04.15 to 18.05.15 | Annual Maintenance Annual Maintenance |

E10: Generation Program for the month of April’15.

Generation schedule for the month of April’15 furnished by OHPC are given below.

| Name of Hydro Gen. Station | Generation Programme (MW) | Reservoir Level as on 01.03.14 | Reservoir Level as on 01.03.15 | MDDL | High Flood Reservoir Level |
| --- | --- | --- | --- | --- | --- |
|  | April’15 |  |  |  |  |
| HPS, Burla | 40+30 | 622.52ft | 618.89ft | 590 ft. | 630 ft. |
| Balimela | 80 | 1503.50ft ft | 1501.30ft | 1440 ft. | 1516 ft. |
| Rengali | 80 | 121.70mt 1.78mt mtr mt | 120.43mt mt | 109.72mtr mtr mtr. | 123.5 mtr. |
| U.Kolab | 80 | 854.24mt mt | 854.81mt | 844 mtr mtmtr. | 858 mtr. |
| U.Indravati | 300 | 639.70mt mt | 637.84mt mt | 625mtr mtr mtr. | 642 mtr |
| MKD (O/D) | 30 | 2740.70ft ft | 2735.65ft ft | 2685 ft. | 2750 ft. |
| TOTAL | 640 |  |  |  |  |

PART F: OTHER ISSUES

F1.  Date and Venue of the next (85th) PSOC meeting:

The date and venue of 85th PSOC meeting shall be intimated to all the Members.

ANNEXURE