## Sheet1
Details of outage of transmission elements during cyclone " YAAS"
Sl.No. | Date | Outage time (Hrs) | Name of element | Reason | Restoration time/ date | Remarks
1 | 25.5.2021 | 20:40 | 132 kV Bhadrak-DPCL-I | E/F | 21:35/26.5.2021
|  | 21:46 | 132 kV Paradeep-PPT-II | R ph, O/C | 07:11/26.5.2021
|  | 21:33 | 132 kV Paradeep-IFFCO-II | R,Y,B ph O/C | 17:18/26.05.2021
|  | 16:48 | Auto-III at Paradeep | PRV Operated | 15:30/27.05.2021
|  | 17:14 | 160 MVA Auto II at Bhadrak | Over fluxing | 09:07/26.05.2021
2 | 26.5.2021 | 2:19 | 132 kV Kendrapara-Paradeep | O/C, E/F | 17:15/26.05.2021
|  |  | 132 kV Paradeep-Marsaghai | O/C, E/F | 2.44/26.05.2021
|  |  | 132 kV Marsaghai-Kendrapara | SOTF | 3.06/26.05.2021
|  | 6:26 | 132 kV Bhadrak-Soro | Y-B ph Fault | 12:01/27.05.2021
|  | 7:14 | 132 kV Paradeep-PPT-II | R ph, O/C | 12.29/26.05.2021
|  | 8:26 | Auto III at Bhadrak | REF | 20:21/26.05.2021
|  | 9:42 | 132 kV Balasore- Udala | O/C, E/F | 18:46/26.05.2021
|  | 9:24 | 63 MVA TRF III at Balasore | REF, Differential relay | 17:54/27.05.2021
|  | 11:13 | 132 kV Balasore- Basta | E/F | 14:34/27.05.2021
|  | 10:04 | 132 kV Duburi Old- Jajpur Road CKT II | DP relay | 11:57/27.05.2021
|  | 16:20 | 220 kV N.Duburi-Balasore | YB ph fault | 20:08/27.05.2021
|  | 17:19 | 132 kV Rourkela-B.K.Steel | DP, RYB ph fault | 15:38/27.05.2021