## 04.12.2021
Tripping details due to JAWAD
SL NO | Name of elements | Reason | Time of tripping | Time of Restoration | Remarks
1 | 220 kv Bhanja nagar Theruvali ckt 2 | Y-B -N ,DP,Zone-1,65.2 Km 2.52 Kamp | 03:01/04.12.2021 | 13.32/04.12.2021
2 | 132 Kv Aska(N)-Aska (o) | B ph Jumper Snapped at Loc No-23 | 03:41/04.12.2021 |  | work is in progress.
3 | 220 Kv Tarkera -Rourkela PG ckt-1 | Y-Ph. drop jumper Snapped at Terkera GSS | 06:20/04.12.2021 | 11:35/04.12.2021

## 05.12.2021
Tripping details due to JAWAD
SL NO | Name of elements | Reason | Time of tripping | Time of Restoration | Remarks
1 | 220 kv Bhanja nagar Theruvali ckt 2 | Y-B -N ,DP,Zone-1,65.2 Km 2.52 Kamp | 03:01/04.12.2021 | 13.32/04.12.2021
2 | 132 Kv Aska(N)-Aska (o) | B ph Jumper Snapped at Loc No-23 | 03:41/04.12.2021 | 14:15/04.12.2021
3 | 220 Kv Tarkera -Rourkela PG ckt-1 | Y-Ph. drop jumper Snapped at Terkera GSS | 06:20/04.12.2021 | 11:35/04.12.2021
4 | 132KV Lapanga- Budhipadar | R ph-E | 06:24/05.12.2022 | 10:34/05.12.2021